## FIM
Table of Recommended Facility Improvement Measures
HVAC Strategies
Tag | Measure Description | Implementation Costs | Projected Savings | Simple Payback (years) | Comments and Recommendations
1.1 | Replace obsolete BAS with approved vendor BAS | 45000 | Sum of FIM 1.2-1.12
1.2 | Implement optimal start routine and keep OA air at minimum | Included in FIM 1.1 |  |  | Requires FIM 1.1
1.3 | Reduce minimum flow settings in VAV terminals | Included in FIM 1.1 |  |  | Requires FIM 1.1 |  |  | % savings
1.4 | Relax zone cooling setpoints | Included in FIM 1.1 |  |  | Requires FIM 1.1 |  |  | % savings
1.5 | Implement dynamic SA duct static pressure setpoint reset | Included in FIM 1.1 |  |  | Requires FIM 1.1
1.6 | Tune VFD and actuator PID loops to match span range | Included in FIM 1.1 |  |  | Requires FIM 1.1
1.7 | Implement demand-control ventilation |  |  |  | Requires FIM 1.1
1.8 | Implement supply air temperature setpoint reset |  | 250 | 10 | Requires FIM 1.1. Implementation cost assumes two zone relative humidity sensors per AHU
1.9 | Link occupancy sensors with VAV systems to set back temperatures |  |  |  | Link to lighting occ sensor fim, Requires FIM 1.1
1.1 | Digitize project records and equipment information in BAS graphics |  | N/A | N/A | Requires FIM 1.1. Savings will be primarily O&M labor, as this FIM improves troubleshooting and response capabilities
1.11 | Damper position programming |  |  |  | Currently AHU-4 has the RAD commanded to 100% if the OAD damper is commanded to anything less than 100%. VFD speed can be reduced by reducing the total static pressure across the unit.
1.12 | Replace damaged/broken CHW DP sensors |  |  |  | The CHW DP sensor was reading 0 psi in the data we were provided and at the time of the building walk through. This sensor should be replaced and a backup DP sensor should be added. The sensor appears to be working fine according to trending log.
1.13 | Reset unoccupied dehumiditification setpoints |  |  |  | Currently the unoccupied dehumidity sequence begins when the sensors reads 70% RH and ends at 65%. It is suggested to reset this to ON at 60% and OFF under 55%.
1.14 | Retune DP dynamic DP setpoint |  |  |  | Once the DP sensor for the CHW system has been replaced the system should be rebalanced with T&B.
1.15 | Service dampers at OAD |  |  |  | Specifically for AHU-3 the OA setpoint is not being met and the most likely cause is faulty damper control. It would be worthwhile to service all damper actuators while the technician is on hand.
1.16 | Check for air leaks in HVAC duct system and seal ductwork
1.17 | Rebalance airside and hydronic HVAC systems after BAS replacement | 5000 | N/A | N/A | This will be mandatory to calibrate the new BAS
1.18 | Install a bypass around the CHW pumps | 2500 | 600 | 5
1.19 | Implement dynamic CHW differential pressure setpoint reset | No Cost | 100 | Immediate
1.2 | Replace all pneumatic controls with DDC |  |  |  | There are roughly 50 pneumatic controls in Building 45. DDCs will increase interoperability with the SkySpark system, improve comfort, and reduce system seeking by the AHUs. | #REF! | kgCO2e/ft2
1.21 | Clean ducts of debris |  | N/A | N/A | Numerous vents in Building 45 showed signs of dirt and debris collecting on and around the vents. | #REF!
1.22 | Consider a displacement air ventilation strategy | Further Analysis Required | Further Analysis Required | Further Analysis Required | The high ceilings in large open spaces found in the first and second floor of Building 45 create a large cubic footage that is conditioned unnecessiarly. This strategy would focus cooling efforts on the occupied spaces only.
Lighting Strategies
Tag | Measure Description | Implementation Costs | Projected Savings | Simple Payback (years) | Comments and Recommendations
2.1 a | Replace existing T8 to LED tube replacements | a) $14,000 | a) $2,500 | a) 6 | The majority of lighting has already been upgraded to LED's. The lighting that has not been upgraded is identified in the Notable Conditions section.
2.1 b | Install LED retrofit-kits | b) $18,800 | b) $2,800 | b) 7 | The majority of lighting has already been upgraded to LED's. The lighting that has not been upgraded is identified in the Notable Conditions section.
2.1 c | Install LED fixtures | c) $21,000 | c) $3,000 | c) 7 | The majority of lighting has already been upgraded to LED's. The lighting that has not been upgraded is identified in the Notable Conditions section.
2.2 | Upgrade personal / desk incandesent and fluorescent bulbs to LED
2.3 | Integrate lighting control system into BAS and align lighting system schedule to correspond to building occupancy schedule | Further Analysis Required | Further Analysis Required | Further Analysis Required
2.4 | Implement a daylighting scheme |  |  |  | There is considerable light that comes in through the numerous windows. Especially in the office space on the third and fourth floor lighting could be reduced with the addition of photocells in appropriate office spaces.
Building Envelope Strategies
Tag | Measure Description | Implementation Costs | Projected Savings | Simple Payback (years) | Comments and Recommendations
3.1 | Power wash the roof |  |  |  | The roof is currently dirty and is absorbing more heat than it would with with a simple power wash.
Other Facility Improvement Measure Strategies
Tag | Measure Description | Implementation Costs | Projected Savings | Simple Payback (years) | Comments and Recommendations
4.1 | Install electrical utility submeter |  | N/A | N/A
4.2 | Implement a Floor Captain policy | No Cost |  | Immediate
4.3 | Install occupancy/smart power strips to ensure plugloads are shut off after hours
4.4 | Implement IT policy for computer shutoff | No Cost |  | Immediate
4.5 | Rooftop Solar Photovoltaic Array
4.6 | Commission all FIMS | TBD | N/A | N/A
4.7 | Develop a systems manual for updated systems | TBD | N/A | N/A
4.8 | Implement Sky Spark FDD after BAS upgrade | No Cost | N/A | N/A
4.9 | Install water utility submeter |  |  |  | Water should be metered seperately for Building 45 and Building 94 to better identify areas of waste.
0.33929
78.0357

## FIM_ImaneUpdate
Table of Recommended Facility Improvement Measures
HVAC Strategies
Tag | Measure Description | Implementation Costs | Projected Savings | Simple Payback (years) | Comments and Recommendations
1.1 | Replace obsolete BAS with approved vendor BAS | 45000 | Sum of FIM 1.2-1.12
1.2 | Implement optimal start routine and keep OA air at minimum | Included in FIM 1.1 |  |  | Requires FIM 1.1
1.3 | Reduce minimum flow settings in VAV terminals | Included in FIM 1.1 |  |  | Requires FIM 1.1
1.4 | Relax zone cooling setpoints | Included in FIM 1.1 |  |  | Requires FIM 1.1
1.7 | Implement dynamic SA duct static pressure setpoint reset | Included in FIM 1.1 |  |  | Requires FIM 1.1
1.8 | Tune VFD and actuator PID loops to match span range | Included in FIM 1.1 |  |  | Requires FIM 1.1
1.9 | Implement demand-control ventilation |  |  |  | Requires FIM 1.1
1.1 | Implement supply air temperature setpoint reset |  | 250 | 10 | Requires FIM 1.1. Implementation cost assumes two zone relative humidity sensors per AHU
1.11 | Link occupancy sensors with VAV systems to set back temperatures |  |  |  | Link to lighting occ sensor fim, Requires FIM 1.1
1.12 | Digitize project records and equipment information in BAS graphics |  | N/A | N/A | Requires FIM 1.1. Savings will be primarily O&M labor, as this FIM improves troubleshooting and response capabilities
1.13 | Damper position programming |  |  |  | Currently AHU-4 has the RAD commanded to 100% if the OAD damper is commanded to anything less than 100%. VFD speed can be reduced by reducing the total static pressure across the unit.
1.14 | Check for air leaks in HVAC duct system and seal ductwork
1.15 | Rebalance airside and hydronic HVAC systems after BAS replacement | 5000 | N/A | N/A | This will be mandatory to calibrate the new BAS
1.18 | Install a bypass around the CHW pumps | 2500 | 600 | 5
1.21 | Implement dynamic CHW differential pressure setpoint reset | No Cost | 100 | Immediate |  | same as 1.16
1.12 | Replace damaged/broken CHW DP sensors |  |  |  | The CHW DP sensor was reading 0 psi in the data we were provided and at the time of the building walk through. This sensor should be replaced and a backup DP sensor should be added. The sensor appears to be working fine according to trending log. | BAS contractor to verify function for reuse
1.13 | Reset unoccupied dehumiditification setpoints |  |  |  | Currently the unoccupied dehumidity sequence begins when the sensors reads 70% RH and ends at 65%. It is suggested to reset this to ON at 60% and OFF under 55%.
1.21 | Retune DP dynamic DP setpoint |  |  |  | Once the DP sensor for the CHW system has been replaced the system should be rebalanced with T&B.
1.15 | Service dampers at OAD |  |  |  | Specifically for AHU-3 the OA setpoint is not being met and the most likely cause is faulty damper control. It would be worthwhile to service all damper actuators while the technician is on hand.
1.2 | Replace all pneumatic controls with DDC |  |  |  | There are roughly 50 pneumatic controls in Building 45. DDCs will increase interoperability with the SkySpark system, improve comfort, and reduce system seeking by the AHUs. | incl w 1.1
1.21 | Clean ducts of debris |  | N/A | N/A | Numerous vents in Building 45 showed signs of dirt and debris collecting on and around the vents.
1.22 | Consider a displacement air ventilation strategy | Further Analysis Required | Further Analysis Required | Further Analysis Required | The high ceilings in large open spaces found in the first and second floor of Building 45 create a large cubic footage that is conditioned unnecessiarly. This strategy would focus cooling efforts on the occupied spaces only.
Lighting Strategies
Tag | Measure Description | Implementation Costs | Projected Savings | Simple Payback (years) | Comments and Recommendations
2.1 a | Replace existing T8 to LED tube replacements | a) $14,000 | a) $2,500 | a) 6 | The majority of lighting has already been upgraded to LED's. The lighting that has not been upgraded is identified in the Notable Conditions section.
2.1 b | Install LED retrofit-kits | b) $18,800 | b) $2,800 | b) 7 | The majority of lighting has already been upgraded to LED's. The lighting that has not been upgraded is identified in the Notable Conditions section.
2.1 c | Install LED fixtures | c) $21,000 | c) $3,000 | c) 7 | The majority of lighting has already been upgraded to LED's. The lighting that has not been upgraded is identified in the Notable Conditions section.
2.2 | Upgrade personal / desk incandesent and fluorescent bulbs to LED
2.3 | Integrate lighting control system into BAS and align lighting system schedule to correspond to building occupancy schedule | Further Analysis Required | Further Analysis Required | Further Analysis Required
2.4 | Implement a daylighting scheme |  |  |  | There is considerable light that comes in through the numerous windows. Especially in the office space on the third and fourth floor lighting could be reduced with the addition of photocells in appropriate office spaces.
Building Envelope Strategies
Tag | Measure Description | Implementation Costs | Projected Savings | Simple Payback (years) | Comments and Recommendations
3.1 | Power wash the roof |  |  |  | The roof is currently dirty and is absorbing more heat than it would with with a simple power wash.
Other Facility Improvement Measure Strategies
Tag | Measure Description | Implementation Costs | Projected Savings | Simple Payback (years) | Comments and Recommendations
4.1 | Install electrical utility submeter |  | N/A | N/A
4.2 | Implement a Floor Captain policy | No Cost |  | Immediate
4.3 | Install occupancy/smart power strips to ensure plugloads are shut off after hours
4.4 | Implement IT policy for computer shutoff | No Cost |  | Immediate
4.5 | Rooftop Solar Photovoltaic Array | 505800 | 37000 | 13.6703
4.6 | Commission all FIMS | TBD | N/A | N/A
4.7 | Develop a systems manual for updated systems | TBD | N/A | N/A
4.8 | Implement Sky Spark FDD after BAS upgrade | No Cost | N/A | N/A
4.9 | Install water utility submeter |  |  |  | Water should be metered seperately for Building 45 and Building 94 to better identify areas of waste.

## Pivot
People, Simultanious Heat/Cool, and OA/Envelope/Infiltration found in Energy Plus Energy Model Report.
Row Labels | Sum of kBtu/yr | Sum of kWh/yr | Sum of W/ft2 | Sum of kBtu/ft2-yr | Sum of Demand Watt | [6 empty] | Summation of CHW Load, kBtu/Year
Lighting | 1021204.1735 | 299285.4 | 4.9217 | 16.7936 | 54448 | [6 empty] | Load Source | CEP kWh | CHW kBtu | % of Total CHW Load
Mechanical | 728603.6963 | 213532.665 | 3.5115 | 11.9818 | 37535 | [6 empty] | Plug Load | 16404.6514 | 55975 | 25.37%
Plug Load | 841647.1723 | 246662.4375 | 4.0563 | 13.8408 | 110361 | [6 empty] | Lighting | 40729.8407 | 138976 | 62.98%
DHW | 78462.1969 | 22995 | 0.37815 | 1.2903 | 16000 | [6 empty] | People | 2756.04 | 9404 | 4.261%
Elevator | 348269.4059 | 102067.6875 | 1.6785 | 5.7273 | 37285 | [6 empty] | Simultanious Heat/Cool | 87.9213 | 300 | 0.1359%
Pump | 208961.6435 | 61240.6125 | 1.0071 | 3.4364 | 22371 | [6 empty] | OA/Envelope/Infiltration | 4695.2911 | 16021 | 7.26%
Electrical | 164396.9839 | 48180 | 0.79232 | 2.7035 | 8800 | [6 empty] | Totals | 64673.7445 | 220676 | 100%
Heating | 105363.5215 | 30879 | 0.5078 | 1.7327 | 282000
Grand Total | 3496908.7938 | 1024842.8025 | 16.8535 | 57.5064 | 568800
Equipment Type | kBtu/yr | kBtu/ft2-yr | W/ft2 | kWh/yr | OS - kBtu/yr | % Diff OS/Spreadsheet | Notes:
Electrical-Parasitic | 164396.9839 | 2.7035 | 0.79232 | 48180 | 164396.9839 | 100%
Heating | 105363.5215 | 1.7327 | 0.5078 | 30879 | 43258 | 41.06%
Lighting | 1021204.1735 | 16.7936 | 4.9217 | 299285.4 | 1054428 | 103.3%
Fan | 728603.6963 | 11.9818 | 3.5115 | 213532.665 | 365895 | 50.22%
Plug Load | 841647.1723 | 13.8408 | 4.0563 | 246662.4375 | 853727 | 101.4%
Pump | 208961.6435 | 3.4364 | 1.0071 | 61240.6125 | 77702 | 37.18%
CHW | 4189503.0121 | 68.8961 | 0 | 1225622.225 | 4003390 | 95.56%
DHW | 78462.1969 | 1.2903 | 0.37815 | 22995 | 78462 | 100%
Grand Total | 7259680.2032 | 119.385 | 14.7968 | 2125402.34 | 5544673 | 76.38%
% Difference Excel Model/Utility |  | Utility kBtu/yr |  | % Difference OS/Utility
Utility/Est (%) | 92.36% | 7859943.7669 |  | 70.54%
Estimated Tonnage/Yr from Lighting on CHW
19.1871
| HVAC Zone Eq & Other Sensible Air Heating [kBtu] | HVAC Zone Eq & Other Sensible Air Cooling [ton-hrs] | HVAC Terminal Unit Sensible Air Heating [kBtu] | HVAC Terminal Unit Sensible Air Cooling [ton-hrs] | HVAC Input Heated Surface Heating [kBtu] | HVAC Input Cooled Surface Cooling [ton-hrs] | People Sensible Heat Addition [kBtu] | Lights Sensible Heat Addition [kBtu] | Equipment Sensible Heat Addition [kBtu] | Window Heat Addition [kBtu] | Interzone Air Transfer Heat Addition [kBtu] | Infiltration Heat Addition [kBtu] | Opaque Surface Conduction and Other Heat Addition [kBtu] | Equipment Sensible Heat Removal [kBtu] | Window Heat Removal [kBtu] | Interzone Air Transfer Heat Removal [kBtu] | Infiltration Heat Removal [kBtu] | Opaque Surface Conduction and Other Heat Removal [kBtu]
BLOCKS-20823_EDUCATION_1_CORE | 0 | 0 | 0.31 | -68473.32 | 0 | 0 | 261028.951 | 361027.939 | 285235.496 | 37058.126 | 0 | 3676.385 | 18.125 | 0 | -13080.21 | 0 | -21857.24 | -90860.65
BLOCKS-20824_OFFICE_1_CORE | 0 | 0 | 9.406 | -55479.68 | 0 | 0 | 63752.704 | 347050.089 | 220456.056 | 74234.239 | 0 | 4530.39 | 2354.035 | 0 | -24432.95 | 0 | -21752.75 | -3.28
BLOCKS-20825_OFFICE_1_CORE | 0 | 0 | 265.817 | -54581.79 | 0 | 0 | 63752.704 | 347050.089 | 220456.056 | 74129.114 | 0 | 5025.888 | 42.599 | 0 | -23674.77 | 0 | -23396.86 | -8188.7
PNNL_ASSET_RATING_OFFICE_SPACE_TYPE_MID_PLENUM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 926.18 | 6964.786 | 0 | 0 | 0 | -7890.97 | 0
PNNL_ASSET_RATING_OFFICE_SPACE_TYPE_TOP_PLENUM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 899.065 | 7529.454 | 0 | 0 | 0 | -8428.52 | 0
PNNL_ASSET_RATING_SCHOOL_SPACE_TYPE_MID_PLENUM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 963.533 | 7436.758 | 0 | 0 | 0 | -8400.29 | 0
Total Facility | 0 | 0 | 275.532 | -178534.79 | 0 | 0 | 388534.36 | 1055128.117 | 726147.609 | 185421.479 | 0 | 16021.44 | 24345.756 | 0 | -61187.93 | 0 | -91726.62 | -99052.62
Sensible Heat Gain Summary.
HVAC Terminal Unit [kBtu] |  |  | 275.532
People Sensible Heat Addition [kBtu] |  |  | 388534.36
Lights Sensible Heat Addition [kBtu] |  |  | 1055128.117
Equipment Sensible Heat Addition [kBtu] |  |  | 726147.609
Window Heat Addition [kBtu] |  |  | 185421.479
Infiltration Heat Addition [kBtu] |  |  | 16021.44
Opaque Surface Conduction and Other Heat Addition [kBtu] |  |  | 24345.756
Window Heat Removal [kBtu] |  |  | -61187.93
Infiltration Heat Removal [kBtu] |  |  | -91726.62
Opaque Surface Conduction and Other Heat Removal [kBtu] |  |  | -99052.62
Total (kBtu) |  |  | 2143907.123

## Lighting_Pivot
Row Labels | Sum of Equipment Count | Sum of Demand Watt | Sum of Spec Wattage | Sum of kWh/yr |  |  | This table may be used to quickly estimate the cost of lighting replacements. The total should be recorded in the Est. Install Cost cell associated with the particular equipment you are building an estimate for.
Lighting | 1103 | 54448 | 9890 | 299285.4
1 .5*4 2 | 1 | 24 | 24 | 131.4 | 2 |  | Equipment Count | Worker $/Hr | Fixtures/Hr | Equipment Cost | Total
1 2' LED | 1 | 12 | 12 | 65.7 | 1 | ED | 4 | 150 | 1 | 300 |  |  |  |  | 100
1 2*2 3 | 1 | 36 | 36 | 197.1 | 3 |  | Installation Cost |  | 600 | 1200 | 1800 |  |  |  | 13 | Column1
1 2*4 1 | 1 | 12 | 12 | 65.7 | 1 | [9 empty] | 13
1 2*4 3 | 2 | 72 | 72 | 394.2 | 3 |  | Safety Factor in Pricing of (Current as of 2018/04/15) |  |  |  | Calibration Check |  |  |  | 13 | Mean | 36.4051
1 2*4*3 | 1 | 36 | 36 | 197.1 | 3 |  | LED Replacement | Listed Cost | Est. Equip Cost | Est. Install Cost (Use Quick Table) | Exp Payback (Yr) | Exp Savings/Yr |  |  | 13 | Standard Error | 2.0963
1 4' underdesk | 1 | 12 | 12 | 65.7 | 1 |  | T8 | 9 | 20 | 11820 | 5 | 2364 |  |  | 13 | Median | 40
1 4p 2b recessed | 1 | 36 | 36 | 197.1 | 2 |  | Trougher Replace 2*4 | 80 | 100 | 21000 | 7 | 3000 | 3010 |  | 13 | Mode | 43
10 2*4 3 | 10 | 360 | 36 | 1971 | 30 |  | Trougher Replace 2*2 | 55 | 70 | 70 | 7 | 10 |  |  | 13 | Standard Deviation | 18.6324
10 4p 2b | 10 | 360 | 36 | 1971 | 20 |  | CFL | 13 | 20 | 2370 | 5 | 474 | 2838 |  | 13 | Sample Variance | 347.1672
10 4pin 2bulb 32w per bulb recessed can | 10 | 640 | 64 | 3504 | 20 |  | Retrofit Kit 2*4 | 82 | 100 | 18666.67 | 7 | 2666.6671 | 2680.9529 |  | 13 | Kurtosis | 0.14566
100W desk lamp | 1 | 100 | 100 | 547.5 | 1 |  | Retrofit Kit 2*2 | 80 | 100 | 100 | 7 | 14.2857 |  | 7.6 | 13 | Skewness | 0.46526
11 4p 2b | 22 | 792 | 72 | 4336.2 | 22 | [9 empty] | 13 | Range | 87
11 4p 2b | 11 | 396 | 36 | 2168.1 | 22 |  | Current Exit sign |  | LED Exit | [5 empty] | 13 | Minimum | 13
11 4p 2b 32W recessed can | 11 | 704 | 64 | 3854.4 | 22 |  | Avg. Count/Floor | Wattage | Total Wattage | [5 empty] | 13 | Maximum | 100
11 4p 2b 32W recessed can | 11 | 704 | 64 | 3854.4 | 22 |  | 10 | 20 | 200 | [5 empty] | 13 | Sum | 2876
11 4p 2b recessed | 22 | 792 | 72 | 4336.2 | 22 |  | Annual kWh Current | 1752 | Wattage | [5 empty] | 13 | Count | 79
11 4p 2b recessed 32W | 11 | 396 | 36 | 2168.1 | 22 |  | Proposed kWh | 438 | 5 | [5 empty] | 13 | Confidence Level(95.0%) | 4.1734
11 4p 2b recessed can | 11 | 396 | 36 | 2168.1 | 22 |  | Installation Cost | 333.3333 | Cost | [5 empty] | 13
12 4p 2b recessed 32W | 12 | 432 | 36 | 2365.2 | 24 |  | Equipment Cost | 400 | 40 | [5 empty] | 13
13 W | 13 | 169 | 13 | 925.275 | 1 |  | Annual Saving | 140.0899 | Total Wattage | [5 empty] | 20
13 w cfl desk lamp | 1 | 13 | 13 | 71.175 | 1 |  | Payback (yrs) | 5.2347 | 50 | [5 empty] | 20
13w cfl | 13 | 169 | 13 | 925.275 | 1 | [9 empty] | 20
13w CFL desklamp | 1 | 13 | 13 | 71.175 | 1 |  | Count of 2*4 Fixtures per Floor |  | Actual Watts/Fix | Proposed Watt/Fix |  |  |  |  | 20
15 2*4 2 dimmable (T12) | 15 | 2700 | 180 | 14782.5 | 30 |  | 140 |  | 90 | 40 |  |  |  |  | 23
15 2*4 3 | 15 | 4050 | 270 | 22173.75 | 45 |  | Average Annual Cost/kWh |  | 0.10661 | This is for buildings with majority 2*4 fixtures. But, is univiersal in that you can always change the wattage per/fixture. |  |  |  |  | 23
15 2*4*3, 1 24/7 | 15 | 540 | 36 | 2956.5 | 15 |  | Number of Floors |  | 1 | [5 empty] | 23
150w hps | 1 | 150 | 150 | 821.25 | 1 |  |  | Actual | Proposed Saving | [5 empty] | 23
16 2*2 3 | 16 | 576 | 36 | 3153.6 | 48 |  | Summed Wattage | 12600 | 5600 | [5 empty] | 23
16 2*4 3 | 16 | 576 | 36 | 3153.6 | 3 |  | Summed kW | 12.6 | 5.6 | [5 empty] | 23
16 4P 2b recessed | 16 | 576 | 36 | 3153.6 | d |  | Current $ kWh used/Floor for lighting: |  | #REF! | Record results below. |  |  |  |  | 23
16 4pin 2bulb 32W per bulb recessed can | 16 | 1024 | 64 | 5606.4 | an |  | Annual LED Bulb Replacement Saving: |  | #REF! | [5 empty] | 23
17 4p 2b recessed | 17 | 612 | 36 | 3350.7 | ed |  | Annual LED + Occ Sensor Savings: |  | #REF! | [5 empty] | 30
2 .5*4 2 | 6 | 144 | 72 | 788.4 | 2 |  | Savings/Floor: |  | #REF! | [5 empty] | 30
2 1*2 1 | 2 | 24 | 12 | 131.4 | 1 |  | LED Bulb Yr Saving: |  | #REF! | [5 empty] | 39
2 100w incandescent track lighting | 2 | 200 | 100 | 1095 | g |  | Payback: | [7 empty] | 40
2 2*2 3 | 2 | 72 | 36 | 394.2 | 3 | [9 empty] | 40
2 2*4 1 | 2 | 24 | 12 | 131.4 | 1 |  | Estimated Switches | Dimming Wired Occ | Installation Cost | [5 empty] | 40
2 2*4 2 | 24 | 576 | 288 | 3153.6 | 2 |  | 80 | 70 | 5600 | [5 empty] | 40
2 2*4 3 | 56 | 2016 | 1008 | 11037.6 | 3 |  | Occ Sensor Saving/Fl: |  | #REF! | [5 empty] | 40
2 2*4 3 | 58 | 2088 | 1044 | 11431.8 | 3 |  | Additional Annual Savings/Yr (25%): |  | #REF! | [5 empty] | 40
2 2*4 5 | 2 | 120 | 60 | 657 | 5 |  | Rooms Available for Daylighting |  | 0 | [5 empty] | 40
2 2*4*3 | 74 | 2664 | 1332 | 14585.4 | *3 |  | Cost/Daylighting Sensor |  | 100 | [5 empty] | 43
2 2*4*3, buzzing ballast | 2 | 72 | 36 | 394.2 | st |  | Daylighting Equipment Cost for Building |  | 0 | [5 empty] | 43
2 24w CFL, 24/7 | 2 | 48 | 24 | 262.8 | /7 | [9 empty] | 43
2 25w incandescent | 2 | 50 | 25 | 273.75 | t |  | Switch Timer $ | # Mech/Elec Rooms | Installation Cost | [5 empty] | 43
2 4' | 2 | 48 | 24 | 262.8 | 4' |  | 20 | 2 | 40 | [5 empty] | 43
2 4' 3 | 2 | 72 | 36 | 394.2 | 3 |  | Bulbs/Mech or Elec Rooms |  | 4 | [5 empty] | 43
2' desklamp | 1 | 9 | 9 | 49.275 | mp |  | Wattage/Bulb (Average is acceptable) |  | 30 | [5 empty] | 43
2*2*3 | 1 | 36 | 36 | 197.1 | *3 |  | 20% Annual Mech Space Light Saving (kWh): |  | #REF! | [5 empty] | 43
2*4*3 | 9 | 324 | 324 | 1773.9 | *3 |  | Saving per Year for Timer Switch Install: |  | #REF! | [5 empty] | 43
20 2*2 led | 20 | 480 | 24 | 2628 | ed | [9 empty] | 43
22 2*4 3 | 22 | 792 | 36 | 4336.2 | 3 | [9 empty] | 43
24 2*4 3 | 24 | 6480 | 270 | 35478 | 3 | [9 empty] | 43
25 2*4 3 | 25 | 900 | 36 | 4927.5 | 3 | [9 empty] | 43
25w incandescent | 1 | 25 | 25 | 136.875 | t | [9 empty] | 43
28 2*4 3 | 28 | 1008 | 36 | 5518.8 | 3 | [9 empty] | 43
3 2*4 3 | 15 | 540 | 180 | 2956.5 | 3 | [9 empty] | 43
3 2*4 3 | 6 | 216 | 72 | 1182.6 | 3 | [9 empty] | 43
3 2*4*3 | 9 | 324 | 108 | 1773.9 | *3 | [9 empty] | 43
3 2*4*3 24/7 | 3 | 108 | 36 | 946.08 | /7 | [9 empty] | 43
32 2*4 3 | 32 | 1152 | 36 | 6307.2 | 3 | [9 empty] | 43
34 4p 2b | 34 | 1224 | 36 | 6701.4 | b | [9 empty] | 53
4 .5*4 2 | 4 | 96 | 24 | 525.6 | 2 | [9 empty] | 53
4 150w hps | 4 | 600 | 150 | 3285 | ps | [9 empty] | 53
4 2*4 3 | 28 | 1008 | 252 | 5518.8 | 3 | [9 empty] | 60
4 2*4*3 | 12 | 432 | 108 | 2365.2 | *3 | [9 empty] | 60
4 2*4*3 24/7 | 4 | 144 | 36 | 788.4 | /7 |  | The below number is unreliable, UNTIL you adjust the Fixtures per floor to reflect the Avg # of rooms w/ 30 of a window providing natural light. | [7 empty] | 60
4 2*4*3, 2 run 24/7 | 4 | 144 | 36 | 788.4 | /7 | [9 empty] | 60
4 4' | 4 | 48 | 12 | 262.8 | 4' | [9 empty] | 60
4 4p 2b | 4 | 144 | 36 | 788.4 | b |  | Daylighting Savings | [7 empty] | 60
4' desklamp | 3 | 36 | 36 | 197.1 | mp |  | #REF! | [7 empty] | 60
40 4p 2b | 40 | 1440 | 36 | 7884 | b | [9 empty] | 60
48 4p 2b | 48 | 1728 | 36 | 9460.8 | 2b | [9 empty] | 60
4p 2b recessed can | 1 | 36 | 36 | 197.1 | an | [9 empty] | 60
5 .5*4 2 | 5 | 120 | 24 | 657 | 2 | [9 empty] | 60
5 2*2 3 | 5 | 180 | 36 | 985.5 | 3 | [9 empty] | 60
5 2*4 3 | 5 | 180 | 36 | 985.5 | 3 | [9 empty] | 63
5 2*4 3 | 10 | 360 | 72 | 1971 | 3 | [9 empty] | 72
5 4' 2 bulb, 24/7 | 5 | 45 | 9 | 246.375 | /7 | [9 empty] | 25
50w halogen quarts | 1 | 50 | 50 | 273.75 | ts
6 2*2*3 24/7 | 6 | 216 | 36 | 1182.6 | /7
6 2*4 3 | 6 | 216 | 36 | 1182.6 | 3
6 2*4 3 | 6 | 216 | 36 | 1182.6 | 3
6 2*4*3 | 6 | 216 | 36 | 1182.6 | *3
60W | 1 | 60 | 60 | 328.5 | 0W
60W desk lamp | 1 | 60 | 60 | 328.5 | mp
7 1*2 1 | 7 | 84 | 12 | 459.9 | 1
7 2*2*3 | 7 | 252 | 36 | 1379.7 | *3
7 2*4 3 | 7 | 252 | 36 | 1379.7 | 3
7 2*4*3 24/7 | 7 | 252 | 36 | 2207.52 | /7
7 4p 2b | 7 | 252 | 36 | 1379.7 | 2b
7 4p 2b recessed | 14 | 504 | 72 | 2759.4 | ed
7 50w halogen a19 , 24/7 | 7 | 350 | 50 | 1916.25 | /7
72w desk lamp | 1 | 72 | 72 | 394.2 | mp
8 2*2 3 | 8 | 288 | 36 | 1576.8 | 3
8 4' per floor | 8 | 2304 | 288 | 12614.4 | or
8 4p 2b 32W | 8 | 512 | 64 | 2803.2 | W
8 wall sconce, assume 150w hps | 8 | 1200 | 150 | 6570 | ps
9 2*4 3 | 9 | 324 | 36 | 1773.9 | 3
A19 led desklamp | 1 | 9 | 9 | 49.275 | mp
Cfl | 2 | 26 | 26 | 142.35 | fl
Decorative led | 1 | 9 | 9 | 49.275 | ed
Desk lamp 1 100W | 1 | 100 | 100 | 547.5 | 0W
Desk lamp 13 W | 1 | 13 | 13 | 71.175 | W
Desk lamp 2 60W | 4 | 240 | 120 | 1314 | 0W
Desk lamp 20W | 1 | 20 | 20 | 109.5 | 0W
Desk lamp 60W 1b | 1 | 60 | 60 | 328.5 | 1b
Led | 2 | 24 | 24 | 131.4 | ed
Office lamp 2 75W bulb | 2 | 150 | 75 | 821.25 | lb
(blank) | 2 | 60 | 60 | 328.5 | k)
Grand Total | 1103 | 54448 | 9890 | 299285.4

## Electrical Panels
kVA (est. to nearest ± 2kVA) | Quantity | Avg. Impedance | Summed kVA | Parasitic Loss | % Loss due to Impedances |  | Enter all known Impedances.
15 | 2 | 5% | 30 | 1.5 |  | 12.37% |  | 4.7%
18 | 2 | 5% | 36 | 1.8 |  |  |  | 5.3%
20 | 1 | 5% | 20 | 1 | Total kWh/yr lost |  |  | 5%
25 | 3 | 5% | 75 | 3.75 |  | 133044.1192
30 | 3 | 5% | 90 | 4.5
36 | 1 | 5% | 36 | 1.8 | Total $/yr lost
45 | 1 | 5% | 45 | 2.25 |  | 14184.2779
70 | 1 | 5% | 70 | 3.5
75 | 1 | 5% | 75 | 3.75 | Tons Cooling from waste heat
80 | 1 | 5% | 80 | 4 |  | 20.0037
115 | 3 | 5% | 345 | 17.25
130 | 1 | 5% | 130 | 6.5
175 | 1 | 5% | 175 | 8.75
200 | 1 | 5% | 200 | 10
| 22 |  | 1407 | 70.35

## 17G0157D_EnergyAudit2
Issue # | Stamp | Title | Description | Spec Wattage | Equipment Count | Utilization % | Demand Watt | kWh/yr | Annual Elec $ | W/ft2 | kBtu/yr | kBtu/ft2-yr | Sheet | # Photos | Archived | Date | Last Updated | Created By
1 | AU | AHU | - CHW actuator appears in good condition. No load, no modulation witnessed. - filters are clean. - Siemens and Trane Summit controls appear to be hooked up to AHU 1-1. Siemens is labeled as OA Monitor. - Vent in space is hand closed. | 22371 | 0 | 90% | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 11 | Mechanical | Mar 12, 2018 @ 12:34 | Mar 12, 2018 @ 12:56 | mcoalson@hanson-inc.com
4 | AH | AHU | Leak on AHU 1-1 after the cooling coil. | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 1 | Mechanical | Mar 12, 2018 @ 12:39 | Mar 14, 2018 @ 15:46 | mcoalson@hanson-inc.com
| VAV |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Heating
714 | AH | AHU | Fcu-4 above ceiling | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | Mechanical | Mar 14, 2018 @ 13:35 | Mar 14, 2018 @ 13:37 | nboyd@hanson-inc.com
| VAV |  |  | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Heating
2 | AU | AHU |  | 11185.5 | 1 | 90% | 11185.5 | 55116.5513 | 5876.1596 | 0.90639 | 188065.4792 | 3.0927 | 2nd Floor | 5 | Mechanical | Mar 12, 2018 @ 12:59 | Mar 12, 2018 @ 13:14 | mcoalson@hanson-inc.com
3 | AU | AHU | - light switch is in unacceptable location. If a person enters from the elevator they must walk around AHU 3 to get to the light switch in total darkness. Add light switch or occ sensor. | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 1 | Mechanical | Mar 12, 2018 @ 13:20 | Mar 12, 2018 @ 13:23 | mcoalson@hanson-inc.com
13 | AH | AHU | Erv-1 | 7457 | 1 | 160% | 7457 | 65323.32 | 6964.3373 | 1.0742 | 222892.4198 | 3.6655 | M401 | 3 | Mechanical | Mar 12, 2018 @ 13:49 | Mar 12, 2018 @ 13:50 | nboyd@hanson-inc.com
893 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:11 | Mar 14, 2018 @ 15:11 | nboyd@hanson-inc.com
906 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:15 | Mar 14, 2018 @ 15:16 | nboyd@hanson-inc.com
913 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:19 | Mar 14, 2018 @ 15:19 | nboyd@hanson-inc.com
921 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:25 | Mar 14, 2018 @ 15:25 | mcoalson@hanson-inc.com
922 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:31 | Mar 14, 2018 @ 15:25 | mcoalson@hanson-inc.com
923 | BA | BAS | Energy web srver |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 1 | #N/A | Mar 14, 2018 @ 15:26 | Mar 14, 2018 @ 15:27 | nboyd@hanson-inc.com
928 | BA | BAS | Tracer BCU |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 2 | #N/A | Mar 14, 2018 @ 15:34 | Mar 14, 2018 @ 15:35 | nboyd@hanson-inc.com
929 | BA | BAS | OA monitor (Siemens) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:36 | Mar 14, 2018 @ 15:36 | nboyd@hanson-inc.com
933 | BA | BAS | Tracer summit panel |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 5 | #N/A | Mar 14, 2018 @ 15:43 | Mar 14, 2018 @ 15:48 | nboyd@hanson-inc.com
977 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:55 | Mar 14, 2018 @ 15:56 | nboyd@hanson-inc.com
998 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:04 | Mar 14, 2018 @ 16:00 | mcoalson@hanson-inc.com
1002 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:07 | Mar 14, 2018 @ 16:01 | mcoalson@hanson-inc.com
1005 | BA | BAS | Tstat, always cold |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:01 | Mar 14, 2018 @ 16:01 | nboyd@hanson-inc.com
1043 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:17 | Mar 14, 2018 @ 16:10 | mcoalson@hanson-inc.com
1047 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:14 | Mar 14, 2018 @ 16:14 | nboyd@hanson-inc.com
1076 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:26 | Mar 14, 2018 @ 16:26 | mcoalson@hanson-inc.com
1088 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:28 | Mar 14, 2018 @ 16:29 | mcoalson@hanson-inc.com
1099 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 5 | #N/A | Mar 14, 2018 @ 17:48 | Mar 14, 2018 @ 17:44 | mcoalson@hanson-inc.com
284 | AU | AHU |  | 18642.5 | 1 | 90% | 18642.5 | 91860.9187 | 9793.5994 | 1.5106 | 313442.4653 | 5.1545 | M401 | 0 | Mechanical | Mar 12, 2018 @ 13:28 | Mar 14, 2018 @ 11:58 | mcoalson@hanson-inc.com
1102 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 1 | #N/A | Mar 14, 2018 @ 17:51 | Mar 14, 2018 @ 17:46 | mcoalson@hanson-inc.com
632 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 12, 2018 @ 19:45 | Mar 12, 2018 @ 19:39 | mcoalson@hanson-inc.com
633 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 12, 2018 @ 19:40 | Mar 12, 2018 @ 19:40 | nboyd@hanson-inc.com
640 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 12, 2018 @ 19:52 | Mar 12, 2018 @ 19:45 | mcoalson@hanson-inc.com
645 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 12, 2018 @ 19:49 | Mar 12, 2018 @ 19:49 | nboyd@hanson-inc.com
650 | BA | BAS | Tracer panel |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 7 | #N/A | Mar 14, 2018 @ 13:05 | Mar 14, 2018 @ 13:58 | nboyd@hanson-inc.com
653 | BA | BAS | oa monitor |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 2 | #N/A | Mar 14, 2018 @ 13:11 | Mar 14, 2018 @ 13:16 | nboyd@hanson-inc.com
655 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:18 | Mar 14, 2018 @ 13:18 | nboyd@hanson-inc.com
690 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:26 | Mar 14, 2018 @ 13:27 | nboyd@hanson-inc.com
695 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:27 | Mar 14, 2018 @ 13:27 | mcoalson@hanson-inc.com
718 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:42 | Mar 14, 2018 @ 13:42 | nboyd@hanson-inc.com
735 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:56 | Mar 14, 2018 @ 13:56 | nboyd@hanson-inc.com
747 | BA | BAS | T-Stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:12 | Mar 14, 2018 @ 14:06 | mcoalson@hanson-inc.com
749 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:14 | Mar 14, 2018 @ 14:07 | mcoalson@hanson-inc.com
752 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:12 | Mar 14, 2018 @ 14:12 | nboyd@hanson-inc.com
807 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:42 | Mar 14, 2018 @ 14:42 | nboyd@hanson-inc.com
810 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:43 | Mar 14, 2018 @ 14:43 | nboyd@hanson-inc.com
817 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:45 | Mar 14, 2018 @ 14:45 | nboyd@hanson-inc.com
822 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:46 | Mar 14, 2018 @ 14:46 | nboyd@hanson-inc.com
836 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:58 | Mar 14, 2018 @ 14:52 | mcoalson@hanson-inc.com
857 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 15:03 | Mar 14, 2018 @ 14:57 | mcoalson@hanson-inc.com
866 | BA | BAS | T-stat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 15:04 | Mar 14, 2018 @ 14:58 | mcoalson@hanson-inc.com
879 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 15:00 | Mar 14, 2018 @ 15:00 | nboyd@hanson-inc.com
5 | BA | BAS | Tracer controls |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | M401 | 13 | #N/A | Mar 12, 2018 @ 13:28 | Mar 12, 2018 @ 13:33 | nboyd@hanson-inc.com
9 | BA | BAS | Siemens oa control |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | M401 | 1 | #N/A | Mar 12, 2018 @ 13:44 | Mar 12, 2018 @ 13:45 | nboyd@hanson-inc.com
39 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:09 | Mar 12, 2018 @ 14:09 | nboyd@hanson-inc.com
42 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:16 | Mar 12, 2018 @ 14:10 | mcoalson@hanson-inc.com
60 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:18 | Mar 12, 2018 @ 14:18 | nboyd@hanson-inc.com
113 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:37 | Mar 12, 2018 @ 14:31 | mcoalson@hanson-inc.com
114 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:31 | Mar 12, 2018 @ 14:31 | nboyd@hanson-inc.com
115 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:38 | Mar 12, 2018 @ 14:31 | mcoalson@hanson-inc.com
116 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:38 | Mar 12, 2018 @ 14:31 | mcoalson@hanson-inc.com
127 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:33 | Mar 12, 2018 @ 14:33 | nboyd@hanson-inc.com
158 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:38 | Mar 12, 2018 @ 14:38 | nboyd@hanson-inc.com
164 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:46 | Mar 12, 2018 @ 14:39 | mcoalson@hanson-inc.com
193 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:53 | Mar 12, 2018 @ 14:46 | mcoalson@hanson-inc.com
216 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:50 | Mar 12, 2018 @ 14:50 | nboyd@hanson-inc.com
254 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:07 | Mar 12, 2018 @ 15:07 | nboyd@hanson-inc.com
264 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:13 | Mar 12, 2018 @ 15:13 | nboyd@hanson-inc.com
287 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:25 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
342 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:49 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
343 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:50 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
385 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:39 | Mar 12, 2018 @ 18:33 | mcoalson@hanson-inc.com
403 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:43 | Mar 12, 2018 @ 18:37 | mcoalson@hanson-inc.com
424 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:41 | Mar 12, 2018 @ 18:41 | nboyd@hanson-inc.com
437 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:48 | Mar 12, 2018 @ 18:48 | nboyd@hanson-inc.com
440 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:00 | Mar 12, 2018 @ 18:54 | mcoalson@hanson-inc.com
461 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:05 | Mar 12, 2018 @ 18:58 | mcoalson@hanson-inc.com
464 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:05 | Mar 12, 2018 @ 18:59 | mcoalson@hanson-inc.com
488 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:09 | Mar 12, 2018 @ 19:03 | mcoalson@hanson-inc.com
499 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:11 | Mar 12, 2018 @ 19:05 | mcoalson@hanson-inc.com
520 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:07 | Mar 12, 2018 @ 19:07 | nboyd@hanson-inc.com
529 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:14 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
537 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:09 | Mar 12, 2018 @ 19:09 | nboyd@hanson-inc.com
588 | BA | BAS | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:15 | nboyd@hanson-inc.com
603 | BA | BAS |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:23 | Mar 12, 2018 @ 19:16 | mcoalson@hanson-inc.com
438 | AH | AHU | Fcu-5 above ceiling, fcu-3-1 on drawings | 250 | 1 | 90% | 250 | 1231.875 | 131.3343 | 0.020258 | 4203.332 | 0.069124 | VTU3-20 | 0 | Mechanical | Mar 12, 2018 @ 18:49 | Mar 12, 2018 @ 18:51 | nboyd@hanson-inc.com
1100 | BA | BAS | Internet server | 120 | 1 | 160% | 120 | 1051.2 | 112.0719 | 0.017287 | 3586.8433 | 0.058985 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 17:43 | Mar 14, 2018 @ 17:44 | mcoalson@hanson-inc.com
937 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:47 | Mar 14, 2018 @ 15:47 | mcoalson@hanson-inc.com
938 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:47 | Mar 14, 2018 @ 15:47 | mcoalson@hanson-inc.com
1094 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 16:36 | Mar 14, 2018 @ 16:30 | mcoalson@hanson-inc.com
710 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:33 | Mar 14, 2018 @ 13:33 | nboyd@hanson-inc.com
776 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | 2nd Floor | 2 | Plug Load | Mar 14, 2018 @ 14:25 | Mar 14, 2018 @ 14:19 | mcoalson@hanson-inc.com
875 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:59 | Mar 14, 2018 @ 14:59 | nboyd@hanson-inc.com
77 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:29 | Mar 12, 2018 @ 14:23 | mcoalson@hanson-inc.com
99 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:35 | Mar 12, 2018 @ 14:28 | mcoalson@hanson-inc.com
148 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:43 | Mar 12, 2018 @ 14:37 | mcoalson@hanson-inc.com
226 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:59 | Mar 12, 2018 @ 14:52 | mcoalson@hanson-inc.com
239 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:02 | Mar 12, 2018 @ 14:56 | mcoalson@hanson-inc.com
303 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:32 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
307 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:33 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
308 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:33 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
405 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:37 | Mar 12, 2018 @ 18:37 | nboyd@hanson-inc.com
531 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
572 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:13 | Mar 12, 2018 @ 19:13 | nboyd@hanson-inc.com
602 | C | Coffee |  | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:16 | Mar 12, 2018 @ 19:16 | nboyd@hanson-inc.com
1062 | CO | Copier |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:23 | Mar 14, 2018 @ 16:23 | nboyd@hanson-inc.com
1084 | CO | Copier |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:27 | Mar 14, 2018 @ 16:27 | mcoalson@hanson-inc.com
713 | CO | Copier |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:34 | Mar 14, 2018 @ 13:34 | nboyd@hanson-inc.com
769 | CO | Copier |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:16 | Mar 14, 2018 @ 14:16 | nboyd@hanson-inc.com
858 | CO | Copier |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:57 | nboyd@hanson-inc.com
21 | CO | Copier | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:11 | Mar 12, 2018 @ 14:05 | mcoalson@hanson-inc.com
413 | CO | Copier |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:40 | Mar 12, 2018 @ 18:40 | nboyd@hanson-inc.com
1000 | DT | Desktop | 2 Count | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:06 | Mar 14, 2018 @ 16:00 | mcoalson@hanson-inc.com
885 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:09 | Mar 14, 2018 @ 15:09 | mcoalson@hanson-inc.com
895 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:13 | Mar 14, 2018 @ 15:13 | nboyd@hanson-inc.com
899 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:15 | Mar 14, 2018 @ 15:15 | mcoalson@hanson-inc.com
900 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:15 | Mar 14, 2018 @ 15:15 | mcoalson@hanson-inc.com
901 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:15 | Mar 14, 2018 @ 15:15 | mcoalson@hanson-inc.com
152 | T8 | Light Fixture | 2' desklamp | 9 | 1 | 100% | 9 | 49.275 | 5.2534 | 0.00081032 | 168.1333 | 0.0027649 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:37 | Mar 12, 2018 @ 14:37 | nboyd@hanson-inc.com
954 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:52 | Mar 14, 2018 @ 15:52 | nboyd@hanson-inc.com
958 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:52 | Mar 14, 2018 @ 15:52 | mcoalson@hanson-inc.com
982 | LF | Lighting Fixture | A19 led desklamp | 9 | 1 | 100% | 9 | 49.275 | 5.2534 | 0.00081032 | 168.1333 | 0.0027649 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:56 | Mar 14, 2018 @ 15:58 | nboyd@hanson-inc.com
967 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:53 | Mar 14, 2018 @ 15:53 | nboyd@hanson-inc.com
968 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:54 | Mar 14, 2018 @ 15:54 | mcoalson@hanson-inc.com
979 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:56 | Mar 14, 2018 @ 15:56 | nboyd@hanson-inc.com
980 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:56 | Mar 14, 2018 @ 15:56 | mcoalson@hanson-inc.com
983 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:57 | Mar 14, 2018 @ 15:57 | mcoalson@hanson-inc.com
993 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:59 | Mar 14, 2018 @ 15:59 | nboyd@hanson-inc.com
997 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:00 | mcoalson@hanson-inc.com
972 | LF | Lighting Fixture | Decorative led | 9 | 1 | 100% | 9 | 49.275 | 5.2534 | 0.00081032 | 168.1333 | 0.0027649 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:54 | Mar 14, 2018 @ 15:55 | nboyd@hanson-inc.com
1008 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:02 | Mar 14, 2018 @ 16:02 | mcoalson@hanson-inc.com
1017 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:03 | mcoalson@hanson-inc.com
1019 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:03 | nboyd@hanson-inc.com
1023 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:10 | Mar 14, 2018 @ 16:03 | mcoalson@hanson-inc.com
1030 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:05 | Mar 14, 2018 @ 16:05 | mcoalson@hanson-inc.com
1038 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:12 | Mar 14, 2018 @ 16:06 | mcoalson@hanson-inc.com
1063 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:23 | Mar 14, 2018 @ 16:23 | nboyd@hanson-inc.com
665 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:21 | Mar 14, 2018 @ 13:21 | nboyd@hanson-inc.com
669 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:23 | Mar 14, 2018 @ 13:23 | mcoalson@hanson-inc.com
670 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:23 | Mar 14, 2018 @ 13:23 | mcoalson@hanson-inc.com
671 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:23 | Mar 14, 2018 @ 13:23 | mcoalson@hanson-inc.com
681 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:25 | Mar 14, 2018 @ 13:25 | mcoalson@hanson-inc.com
696 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:27 | Mar 14, 2018 @ 13:27 | nboyd@hanson-inc.com
703 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:30 | Mar 14, 2018 @ 13:30 | nboyd@hanson-inc.com
708 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:32 | Mar 14, 2018 @ 13:32 | nboyd@hanson-inc.com
739 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:58 | Mar 14, 2018 @ 13:58 | mcoalson@hanson-inc.com
756 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:14 | Mar 14, 2018 @ 14:14 | mcoalson@hanson-inc.com
757 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:14 | Mar 14, 2018 @ 14:14 | mcoalson@hanson-inc.com
773 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:18 | Mar 14, 2018 @ 14:18 | mcoalson@hanson-inc.com
780 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:28 | Mar 14, 2018 @ 14:21 | mcoalson@hanson-inc.com
790 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:32 | Mar 14, 2018 @ 14:32 | mcoalson@hanson-inc.com
798 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:39 | Mar 14, 2018 @ 14:39 | mcoalson@hanson-inc.com
818 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:51 | Mar 14, 2018 @ 14:45 | mcoalson@hanson-inc.com
843 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:54 | Mar 14, 2018 @ 14:54 | mcoalson@hanson-inc.com
844 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:54 | Mar 14, 2018 @ 14:54 | nboyd@hanson-inc.com
856 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:57 | mcoalson@hanson-inc.com
862 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:57 | nboyd@hanson-inc.com
878 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 15:06 | Mar 14, 2018 @ 15:00 | mcoalson@hanson-inc.com
880 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 15:08 | Mar 14, 2018 @ 15:01 | mcoalson@hanson-inc.com
19 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:11 | Mar 12, 2018 @ 14:05 | mcoalson@hanson-inc.com
24 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:05 | Mar 12, 2018 @ 14:05 | nboyd@hanson-inc.com
33 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:08 | Mar 12, 2018 @ 14:08 | nboyd@hanson-inc.com
37 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:15 | Mar 12, 2018 @ 14:09 | mcoalson@hanson-inc.com
63 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:19 | Mar 12, 2018 @ 14:19 | nboyd@hanson-inc.com
67 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:27 | Mar 12, 2018 @ 14:20 | mcoalson@hanson-inc.com
70 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:28 | Mar 12, 2018 @ 14:21 | mcoalson@hanson-inc.com
81 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:24 | Mar 12, 2018 @ 14:24 | nboyd@hanson-inc.com
98 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:35 | Mar 12, 2018 @ 14:28 | mcoalson@hanson-inc.com
100 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:29 | Mar 12, 2018 @ 14:29 | nboyd@hanson-inc.com
106 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:30 | Mar 12, 2018 @ 14:30 | nboyd@hanson-inc.com
118 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:38 | Mar 12, 2018 @ 14:31 | mcoalson@hanson-inc.com
124 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:32 | Mar 12, 2018 @ 14:32 | nboyd@hanson-inc.com
132 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:34 | Mar 12, 2018 @ 14:34 | nboyd@hanson-inc.com
141 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:35 | Mar 12, 2018 @ 14:35 | nboyd@hanson-inc.com
142 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:42 | Mar 12, 2018 @ 14:35 | mcoalson@hanson-inc.com
151 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:37 | Mar 12, 2018 @ 14:37 | nboyd@hanson-inc.com
161 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:45 | Mar 12, 2018 @ 14:39 | mcoalson@hanson-inc.com
167 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:46 | Mar 12, 2018 @ 14:40 | mcoalson@hanson-inc.com
170 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:40 | Mar 12, 2018 @ 14:40 | nboyd@hanson-inc.com
177 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:50 | Mar 12, 2018 @ 14:43 | mcoalson@hanson-inc.com
186 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:45 | Mar 12, 2018 @ 14:45 | nboyd@hanson-inc.com
198 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:53 | Mar 12, 2018 @ 14:47 | mcoalson@hanson-inc.com
199 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:47 | Mar 12, 2018 @ 14:47 | nboyd@hanson-inc.com
210 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:49 | Mar 12, 2018 @ 14:49 | nboyd@hanson-inc.com
214 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:57 | Mar 12, 2018 @ 14:50 | mcoalson@hanson-inc.com
223 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:51 | Mar 12, 2018 @ 14:51 | nboyd@hanson-inc.com
232 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:00 | Mar 12, 2018 @ 14:53 | mcoalson@hanson-inc.com
233 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:00 | Mar 12, 2018 @ 14:53 | mcoalson@hanson-inc.com
250 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:06 | Mar 12, 2018 @ 15:06 | nboyd@hanson-inc.com
271 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:20 | Mar 12, 2018 @ 15:14 | mcoalson@hanson-inc.com
274 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:15 | Mar 12, 2018 @ 15:15 | nboyd@hanson-inc.com
286 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:25 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
292 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:26 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
298 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:30 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
323 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:42 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
327 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:43 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
333 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:45 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
340 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:47 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
346 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:50 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
351 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:51 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
368 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:55 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
369 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:55 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
371 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:57 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
372 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:57 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
373 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:57 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
374 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:57 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
386 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:40 | Mar 12, 2018 @ 18:33 | mcoalson@hanson-inc.com
391 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:41 | Mar 12, 2018 @ 18:35 | mcoalson@hanson-inc.com
398 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:43 | Mar 12, 2018 @ 18:36 | mcoalson@hanson-inc.com
409 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:44 | Mar 12, 2018 @ 18:38 | mcoalson@hanson-inc.com
417 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:47 | Mar 12, 2018 @ 18:40 | mcoalson@hanson-inc.com
420 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:41 | Mar 12, 2018 @ 18:41 | nboyd@hanson-inc.com
445 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:55 | Mar 12, 2018 @ 18:55 | nboyd@hanson-inc.com
457 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:04 | Mar 12, 2018 @ 18:57 | mcoalson@hanson-inc.com
470 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:00 | Mar 12, 2018 @ 19:00 | nboyd@hanson-inc.com
473 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:07 | Mar 12, 2018 @ 19:01 | mcoalson@hanson-inc.com
480 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:09 | Mar 12, 2018 @ 19:02 | mcoalson@hanson-inc.com
484 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:02 | Mar 12, 2018 @ 19:02 | nboyd@hanson-inc.com
492 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:10 | Mar 12, 2018 @ 19:04 | mcoalson@hanson-inc.com
502 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:11 | Mar 12, 2018 @ 19:05 | mcoalson@hanson-inc.com
508 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:05 | Mar 12, 2018 @ 19:05 | nboyd@hanson-inc.com
514 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:12 | Mar 12, 2018 @ 19:06 | mcoalson@hanson-inc.com
526 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:14 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
534 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
542 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:09 | mcoalson@hanson-inc.com
549 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:10 | Mar 12, 2018 @ 19:10 | nboyd@hanson-inc.com
554 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:17 | Mar 12, 2018 @ 19:11 | mcoalson@hanson-inc.com
559 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:18 | Mar 12, 2018 @ 19:12 | mcoalson@hanson-inc.com
567 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:19 | Mar 12, 2018 @ 19:13 | mcoalson@hanson-inc.com
577 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:20 | Mar 12, 2018 @ 19:13 | mcoalson@hanson-inc.com
578 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:14 | Mar 12, 2018 @ 19:14 | nboyd@hanson-inc.com
582 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:21 | Mar 12, 2018 @ 19:15 | mcoalson@hanson-inc.com
593 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:16 | Mar 12, 2018 @ 19:16 | nboyd@hanson-inc.com
597 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:16 | Mar 12, 2018 @ 19:16 | nboyd@hanson-inc.com
599 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:22 | Mar 12, 2018 @ 19:16 | mcoalson@hanson-inc.com
607 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:23 | Mar 12, 2018 @ 19:17 | mcoalson@hanson-inc.com
615 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:18 | Mar 12, 2018 @ 19:18 | nboyd@hanson-inc.com
624 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:28 | Mar 12, 2018 @ 19:22 | mcoalson@hanson-inc.com
924 | E | Electrical | Xfmer |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 1 | Electrical | Mar 14, 2018 @ 15:30 | Mar 14, 2018 @ 15:30 | nboyd@hanson-inc.com
925 | E | Electrical | Xfmer |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 1 | Electrical | Mar 14, 2018 @ 15:31 | Mar 14, 2018 @ 15:32 | nboyd@hanson-inc.com
927 | E | Electrical | ATS |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 1 | Electrical | Mar 14, 2018 @ 15:33 | Mar 14, 2018 @ 15:33 | nboyd@hanson-inc.com
744 | E | Electrical | Intermittent harmonic buzzing above ceiling |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | Electrical | Mar 14, 2018 @ 14:02 | Mar 14, 2018 @ 14:03 | nboyd@hanson-inc.com
794 | E | Electrical | Xfmer |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 1 | Electrical | Mar 14, 2018 @ 14:36 | Mar 14, 2018 @ 14:37 | nboyd@hanson-inc.com
8 | FN | Fan | On roof |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 2 | Fan | Mar 12, 2018 @ 13:43 | Mar 12, 2018 @ 13:44 | mcoalson@hanson-inc.com
10 | FN | Fan | On roof |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 3 | Fan | Mar 12, 2018 @ 13:44 | Mar 12, 2018 @ 13:45 | mcoalson@hanson-inc.com
628 | DT | Desktop |  | 50 | 1 | 90% | 50 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:36 | Mar 12, 2018 @ 19:29 | mcoalson@hanson-inc.com
236 | GL | Glass | Fire door |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 2 | #N/A | Mar 12, 2018 @ 14:54 | Mar 12, 2018 @ 14:55 | nboyd@hanson-inc.com
238 | GL | Glass |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:56 | Mar 12, 2018 @ 14:56 | nboyd@hanson-inc.com
918 | E | Electrical | Xfmer | 8800 | 1 | 100% | 8800 | 48180 | 5136.6307 | 0.79232 | 164396.9839 | 2.7035 | 1st Floor | 1 | Electrical | Mar 14, 2018 @ 15:22 | Mar 14, 2018 @ 15:23 | nboyd@hanson-inc.com
748 | IT | Information technology | 120v 23a ups |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:06 | Mar 14, 2018 @ 14:06 | nboyd@hanson-inc.com
242 | IT | Information technology | 240v 23a ups |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:00 | Mar 12, 2018 @ 15:00 | nboyd@hanson-inc.com
11 | FN | Fan | On roof - fans need a cover to protect from rain infiltration. | 22371 | 1 | 0% | 22371 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 1 | Fan | Mar 12, 2018 @ 13:45 | Mar 12, 2018 @ 13:53 | mcoalson@hanson-inc.com
894 | IT | Information technology | AV cabinet | 120 | 1 | 50% | 120 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:12 | Mar 14, 2018 @ 15:12 | nboyd@hanson-inc.com
1069 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:25 | Mar 14, 2018 @ 16:25 | mcoalson@hanson-inc.com
1079 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:27 | Mar 14, 2018 @ 16:27 | mcoalson@hanson-inc.com
1086 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:28 | Mar 14, 2018 @ 16:28 | nboyd@hanson-inc.com
1091 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:29 | Mar 14, 2018 @ 16:29 | mcoalson@hanson-inc.com
658 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:18 | Mar 14, 2018 @ 13:18 | nboyd@hanson-inc.com
777 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:19 | Mar 14, 2018 @ 14:19 | mcoalson@hanson-inc.com
781 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:21 | Mar 14, 2018 @ 14:21 | mcoalson@hanson-inc.com
47 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:11 | Mar 12, 2018 @ 14:11 | nboyd@hanson-inc.com
54 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:19 | Mar 12, 2018 @ 14:13 | mcoalson@hanson-inc.com
168 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:46 | Mar 12, 2018 @ 14:40 | mcoalson@hanson-inc.com
181 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:50 | Mar 12, 2018 @ 14:44 | mcoalson@hanson-inc.com
187 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:51 | Mar 12, 2018 @ 14:45 | mcoalson@hanson-inc.com
227 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:59 | Mar 12, 2018 @ 14:53 | mcoalson@hanson-inc.com
228 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:59 | Mar 12, 2018 @ 14:53 | mcoalson@hanson-inc.com
229 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:59 | Mar 12, 2018 @ 14:53 | mcoalson@hanson-inc.com
230 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:59 | Mar 12, 2018 @ 14:53 | mcoalson@hanson-inc.com
231 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:59 | Mar 12, 2018 @ 14:53 | mcoalson@hanson-inc.com
279 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:23 | Mar 12, 2018 @ 15:16 | mcoalson@hanson-inc.com
361 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:53 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
530 | LT | Laptop |  | 40 | 1 | 90% | 40 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:14 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
295 | LF | Lighting Fixture | 1 2' LED | 12 | 1 | 100% | 12 | 65.7 | 7.0045 | 0.0010804 | 224.1777 | 0.0036866 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:27 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
716 | T8 | Light Fixture | 1 2*4 1 | 12 | 1 | 100% | 12 | 65.7 | 7.0045 | 0.0010804 | 224.1777 | 0.0036866 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:44 | Mar 14, 2018 @ 13:38 | mcoalson@hanson-inc.com
43 | T8 | Light Fixture | 1 4' underdesk | 12 | 1 | 100% | 12 | 65.7 | 7.0045 | 0.0010804 | 224.1777 | 0.0036866 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:10 | Mar 12, 2018 @ 14:10 | nboyd@hanson-inc.com
166 | T8 | Light Fixture | 4' desklamp | 12 | 1 | 100% | 12 | 65.7 | 7.0045 | 0.0010804 | 224.1777 | 0.0036866 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:39 | Mar 12, 2018 @ 14:42 | nboyd@hanson-inc.com
175 | T8 | Light Fixture | 4' desklamp | 12 | 1 | 100% | 12 | 65.7 | 7.0045 | 0.0010804 | 224.1777 | 0.0036866 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:42 | Mar 12, 2018 @ 14:42 | nboyd@hanson-inc.com
270 | T8 | Light Fixture | 4' desklamp | 12 | 1 | 100% | 12 | 65.7 | 7.0045 | 0.0010804 | 224.1777 | 0.0036866 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:14 | Mar 12, 2018 @ 15:14 | nboyd@hanson-inc.com
1012 | LF | Lighting Fixture | Led | 12 | 1 | 100% | 12 | 65.7 | 7.0045 | 0.0010804 | 224.1777 | 0.0036866 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:03 | nboyd@hanson-inc.com
1013 | LF | Lighting Fixture | Led | 12 | 1 | 100% | 12 | 65.7 | 7.0045 | 0.0010804 | 224.1777 | 0.0036866 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:03 | nboyd@hanson-inc.com
1029 | LF | Lighting Fixture | 13 w cfl desk lamp | 13 | 1 | 100% | 13 | 71.175 | 7.5882 | 0.0011705 | 242.8592 | 0.0039938 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:05 | Mar 14, 2018 @ 16:05 | mcoalson@hanson-inc.com
994 | LF | Lighting Fixture | 13w CFL desklamp | 13 | 1 | 100% | 13 | 71.175 | 7.5882 | 0.0011705 | 242.8592 | 0.0039938 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:59 | Mar 14, 2018 @ 16:00 | nboyd@hanson-inc.com
1010 | LF | Lighting Fixture | Cfl | 13 | 1 | 100% | 13 | 71.175 | 7.5882 | 0.0011705 | 242.8592 | 0.0039938 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:02 | Mar 14, 2018 @ 16:03 | nboyd@hanson-inc.com
1014 | LF | Lighting Fixture | Cfl | 13 | 1 | 100% | 13 | 71.175 | 7.5882 | 0.0011705 | 242.8592 | 0.0039938 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:03 | nboyd@hanson-inc.com
689 | LF | Lighting Fixture | Desk lamp 13 W | 13 | 1 | 100% | 13 | 71.175 | 7.5882 | 0.0011705 | 242.8592 | 0.0039938 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:26 | Mar 14, 2018 @ 13:27 | mcoalson@hanson-inc.com
454 | LF | Lighting Fixture | Desk lamp 20W | 20 | 1 | 100% | 20 | 109.5 | 11.6742 | 0.0018007 | 373.6295 | 0.0061443 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:03 | Mar 12, 2018 @ 18:57 | mcoalson@hanson-inc.com
312 | T8 | Light Fixture | 1 .5*4 2 | 24 | 1 | 100% | 24 | 131.4 | 14.009 | 0.0021609 | 448.3554 | 0.0073732 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:36 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
1073 | T8 | Light Fixture |  | 24 | 1 | 100% | 24 | 131.4 | 14.009 | 0.0021609 | 448.3554 | 0.0073732 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:44 | Mar 14, 2018 @ 16:25 | mcoalson@hanson-inc.com
414 | T8 | Light Fixture | 2 1*2 1 | 12 | 2 | 100% | 24 | 131.4 | 14.009 | 0.0021609 | 448.3554 | 0.0073732 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:46 | Mar 12, 2018 @ 18:40 | mcoalson@hanson-inc.com
208 | T8 | Light Fixture | 2 2*4 1 | 12 | 2 | 100% | 24 | 131.4 | 14.009 | 0.0021609 | 448.3554 | 0.0073732 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:55 | Mar 12, 2018 @ 14:49 | mcoalson@hanson-inc.com
667 | LF | Lighting Fixture | 25w incandescent | 25 | 1 | 100% | 25 | 136.875 | 14.5927 | 0.0022509 | 467.0369 | 0.0076804 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:22 | Mar 14, 2018 @ 13:22 | nboyd@hanson-inc.com
966 | T8 | Light Fixture | 1 2*2 3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:53 | Mar 14, 2018 @ 15:53 | mcoalson@hanson-inc.com
1065 | T8 | Light Fixture | 1 2*4 3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:24 | Mar 14, 2018 @ 16:24 | mcoalson@hanson-inc.com
715 | T8 | Light Fixture | 1 2*4 3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:41 | Mar 14, 2018 @ 13:37 | mcoalson@hanson-inc.com
802 | T8 | Light Fixture | 1 2*4*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:40 | Mar 14, 2018 @ 14:40 | nboyd@hanson-inc.com
745 | LF | Lighting Fixture | 1 4p 2b recessed | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:04 | Mar 14, 2018 @ 14:04 | mcoalson@hanson-inc.com
1077 | T8 | Light Fixture | 2*2*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:26 | Mar 14, 2018 @ 16:26 | nboyd@hanson-inc.com
805 | T8 | Light Fixture | 2*4*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:41 | Mar 14, 2018 @ 14:41 | nboyd@hanson-inc.com
806 | T8 | Light Fixture | 2*4*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:42 | Mar 14, 2018 @ 14:42 | nboyd@hanson-inc.com
808 | T8 | Light Fixture | 2*4*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:42 | Mar 14, 2018 @ 14:43 | nboyd@hanson-inc.com
809 | T8 | Light Fixture | 2*4*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:43 | Mar 14, 2018 @ 14:43 | nboyd@hanson-inc.com
811 | T8 | Light Fixture | 2*4*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:43 | Mar 14, 2018 @ 14:44 | nboyd@hanson-inc.com
812 | T8 | Light Fixture | 2*4*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:44 | Mar 14, 2018 @ 14:44 | nboyd@hanson-inc.com
814 | T8 | Light Fixture | 2*4*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:44 | Mar 14, 2018 @ 14:44 | nboyd@hanson-inc.com
819 | T8 | Light Fixture | 2*4*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:45 | Mar 14, 2018 @ 14:45 | nboyd@hanson-inc.com
820 | T8 | Light Fixture | 2*4*3 | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:46 | Mar 14, 2018 @ 14:46 | nboyd@hanson-inc.com
898 | LF | Lighting Fixture | 4p 2b recessed can | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:15 | Mar 14, 2018 @ 15:15 | nboyd@hanson-inc.com
1027 | T8 | Light Fixture |  | 36 | 1 | 100% | 36 | 197.1 | 21.0135 | 0.0032413 | 672.5331 | 0.01106 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:04 | Mar 14, 2018 @ 16:04 | mcoalson@hanson-inc.com
6 | T8 | Light Fixture | 5 4' 2 bulb, 24/7 | 9 | 5 | 100% | 45 | 246.375 | 26.2669 | 0.0040516 | 840.6664 | 0.013825 | M401 | 0 | Lighting | Mar 12, 2018 @ 13:35 | Mar 12, 2018 @ 13:57 | nboyd@hanson-inc.com
1051 | T8 | Light Fixture | 2 .5*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:17 | Mar 14, 2018 @ 16:17 | mcoalson@hanson-inc.com
1095 | T8 | Light Fixture | 2 .5*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 17:44 | Mar 14, 2018 @ 17:39 | mcoalson@hanson-inc.com
750 | T8 | Light Fixture | 2 .5*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:15 | Mar 14, 2018 @ 14:14 | mcoalson@hanson-inc.com
65 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:26 | Mar 12, 2018 @ 14:20 | mcoalson@hanson-inc.com
107 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:37 | Mar 12, 2018 @ 14:30 | mcoalson@hanson-inc.com
1048 | M | Mechanical | Elevator gear | 37285 | 1 | 50% | 37285 | 102067.6875 | 10881.7771 | 1.6785 | 348269.4059 | 5.7273 | 1st Floor | 3 | Elevator | Mar 14, 2018 @ 16:15 | Mar 14, 2018 @ 16:16 | nboyd@hanson-inc.com
936 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:47 | Mar 14, 2018 @ 15:47 | mcoalson@hanson-inc.com
1093 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 16:36 | Mar 14, 2018 @ 16:30 | mcoalson@hanson-inc.com
680 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:25 | Mar 14, 2018 @ 13:25 | nboyd@hanson-inc.com
709 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:33 | Mar 14, 2018 @ 13:33 | nboyd@hanson-inc.com
766 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:16 | Mar 14, 2018 @ 14:16 | nboyd@hanson-inc.com
768 | MV | Microwave | Toaster | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:16 | Mar 14, 2018 @ 14:16 | nboyd@hanson-inc.com
874 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:59 | Mar 14, 2018 @ 14:59 | nboyd@hanson-inc.com
144 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:43 | Mar 12, 2018 @ 14:36 | mcoalson@hanson-inc.com
304 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:32 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
402 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:37 | Mar 12, 2018 @ 18:37 | nboyd@hanson-inc.com
404 | MV | Microwave | Toaster oven | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:37 | Mar 12, 2018 @ 18:37 | nboyd@hanson-inc.com
406 | MV | Microwave | Toaster | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:37 | Mar 12, 2018 @ 18:37 | nboyd@hanson-inc.com
428 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:43 | Mar 12, 2018 @ 18:43 | nboyd@hanson-inc.com
619 | MV | Microwave |  | 1200 | 1 | 5% | 1200 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:18 | Mar 12, 2018 @ 19:18 | nboyd@hanson-inc.com
678 | FR | Minifridge |  | 57 | 1 | 75% | 57 | 234.0563 | 24.9535 | 0.003849 | 798.6331 | 0.013133 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:24 | Mar 14, 2018 @ 13:24 | nboyd@hanson-inc.com
765 | FR | Minifridge |  | 57 | 1 | 75% | 57 | 234.0563 | 24.9535 | 0.003849 | 798.6331 | 0.013133 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:15 | Mar 14, 2018 @ 14:15 | nboyd@hanson-inc.com
873 | FR | Minifridge |  | 57 | 1 | 75% | 57 | 234.0563 | 24.9535 | 0.003849 | 798.6331 | 0.013133 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:59 | Mar 14, 2018 @ 14:59 | nboyd@hanson-inc.com
78 | FR | Minifridge |  | 57 | 1 | 75% | 57 | 234.0563 | 24.9535 | 0.003849 | 798.6331 | 0.013133 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:23 | Mar 12, 2018 @ 14:23 | nboyd@hanson-inc.com
430 | FR | Minifridge |  | 57 | 1 | 75% | 57 | 234.0563 | 24.9535 | 0.003849 | 798.6331 | 0.013133 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:43 | Mar 12, 2018 @ 18:43 | nboyd@hanson-inc.com
550 | FR | Minifridge |  | 57 | 1 | 75% | 57 | 234.0563 | 24.9535 | 0.003849 | 798.6331 | 0.013133 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:11 | Mar 12, 2018 @ 19:11 | nboyd@hanson-inc.com
618 | FR | Minifridge |  | 57 | 1 | 75% | 57 | 234.0563 | 24.9535 | 0.003849 | 798.6331 | 0.013133 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:18 | Mar 12, 2018 @ 19:18 | nboyd@hanson-inc.com
883 | MS | Miscellaneous | Projector | 308 | 1 | 50% | 308 | 843.15 | 89.891 | 0.013866 | 2876.9472 | 0.047311 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 15:07 | Mar 14, 2018 @ 15:08 | mcoalson@hanson-inc.com
886 | MS | Miscellaneous | Creston media processor | 120 | 1 | 50% | 120 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 15:09 | Mar 14, 2018 @ 15:10 | mcoalson@hanson-inc.com
981 | MS | Miscellaneous | Projector | 308 | 1 | 50% | 308 | 843.15 | 89.891 | 0.013866 | 2876.9472 | 0.047311 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:56 | Mar 14, 2018 @ 15:56 | mcoalson@hanson-inc.com
1050 | MS | Miscellaneous | Instant hot | 4000 | 1 | 10% | 4000 | 2190 | 233.4832 | 0.036014 | 7472.5902 | 0.12289 | 1st Floor | 1 | DHW | Mar 14, 2018 @ 16:16 | Mar 14, 2018 @ 16:16 | mcoalson@hanson-inc.com
642 | MS | Miscellaneous | Server | 120 | 1 | 100% | 120 | 657 | 70.045 | 0.010804 | 2241.7771 | 0.036866 | 2nd Floor | 4 | Plug Load | Mar 12, 2018 @ 19:53 | Mar 12, 2018 @ 19:48 | mcoalson@hanson-inc.com
705 | MS | Miscellaneous | UPS | 276 | 1 | 100% | 276 | 1511.1 | 161.1034 | 0.02485 | 5156.0872 | 0.084792 | 2nd Floor | 3 | Plug Load | Mar 14, 2018 @ 13:37 | Mar 14, 2018 @ 13:37 | mcoalson@hanson-inc.com
720 | MS | Miscellaneous | Water Fountain | 370 | 1 | 75% | 370 | 1519.3125 | 161.979 | 0.024985 | 5184.1094 | 0.085252 | 2nd Floor | 1 | Plug Load | Mar 14, 2018 @ 13:43 | Mar 14, 2018 @ 13:45 | mcoalson@hanson-inc.com
738 | MS | Miscellaneous | Projector | 308 | 1 | 50% | 308 | 843.15 | 89.891 | 0.013866 | 2876.9472 | 0.047311 | 2nd Floor | 1 | Plug Load | Mar 14, 2018 @ 13:57 | Mar 14, 2018 @ 13:57 | mcoalson@hanson-inc.com
791 | MS | Miscellaneous | Projector | 308 | 1 | 50% | 308 | 843.15 | 89.891 | 0.013866 | 2876.9472 | 0.047311 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:32 | Mar 14, 2018 @ 14:32 | mcoalson@hanson-inc.com
797 | MS | Miscellaneous | Projector | 308 | 1 | 50% | 308 | 843.15 | 89.891 | 0.013866 | 2876.9472 | 0.047311 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:39 | Mar 14, 2018 @ 14:39 | mcoalson@hanson-inc.com
816 | MS | Miscellaneous | Creston 3 series audio visual for classroom, runs like a full server? | 120 | 1 | 50% | 120 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 2nd Floor | 3 | Plug Load | Mar 14, 2018 @ 14:44 | Mar 14, 2018 @ 14:51 | mcoalson@hanson-inc.com
821 | MS | Miscellaneous | Projector | 308 | 1 | 50% | 308 | 843.15 | 89.891 | 0.013866 | 2876.9472 | 0.047311 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:52 | Mar 14, 2018 @ 14:46 | mcoalson@hanson-inc.com
296 | MS | Miscellaneous | Word processor | 50 | 1 | 10% | 50 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 1 | Plug Load | Mar 12, 2018 @ 15:29 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
297 | MS | Miscellaneous | Laminator | 1000 | 1 | 10% | 1000 | 547.5 | 58.3708 | 0.0090036 | 1868.1475 | 0.030722 | VTU3-20 | 1 | Plug Load | Mar 12, 2018 @ 15:30 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
306 | MS | Miscellaneous | Toaster sm | 1000 | 1 | 5% | 1000 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:33 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
629 | MS | Miscellaneous | Projector | 308 | 1 | 50% | 308 | 843.15 | 89.891 | 0.013866 | 2876.9472 | 0.047311 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:36 | Mar 12, 2018 @ 19:30 | mcoalson@hanson-inc.com
884 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:08 | Mar 14, 2018 @ 15:08 | mcoalson@hanson-inc.com
896 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:13 | Mar 14, 2018 @ 15:13 | nboyd@hanson-inc.com
897 | M | Monitor | Smart board projector | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 2 | Plug Load | Mar 14, 2018 @ 15:13 | Mar 14, 2018 @ 15:14 | nboyd@hanson-inc.com
902 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:15 | Mar 14, 2018 @ 15:15 | mcoalson@hanson-inc.com
903 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:15 | Mar 14, 2018 @ 15:15 | mcoalson@hanson-inc.com
904 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:15 | Mar 14, 2018 @ 15:15 | mcoalson@hanson-inc.com
905 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:15 | Mar 14, 2018 @ 15:15 | mcoalson@hanson-inc.com
909 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:17 | Mar 14, 2018 @ 15:17 | mcoalson@hanson-inc.com
948 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:51 | Mar 14, 2018 @ 15:51 | nboyd@hanson-inc.com
949 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:51 | Mar 14, 2018 @ 15:51 | nboyd@hanson-inc.com
951 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:51 | Mar 14, 2018 @ 15:51 | nboyd@hanson-inc.com
955 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:52 | Mar 14, 2018 @ 15:52 | mcoalson@hanson-inc.com
956 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:52 | Mar 14, 2018 @ 15:52 | mcoalson@hanson-inc.com
969 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:54 | Mar 14, 2018 @ 15:54 | mcoalson@hanson-inc.com
970 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:54 | Mar 14, 2018 @ 15:54 | mcoalson@hanson-inc.com
984 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:57 | Mar 14, 2018 @ 15:57 | mcoalson@hanson-inc.com
985 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:57 | Mar 14, 2018 @ 15:57 | mcoalson@hanson-inc.com
986 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:57 | Mar 14, 2018 @ 15:57 | mcoalson@hanson-inc.com
995 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:00 | mcoalson@hanson-inc.com
996 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:00 | mcoalson@hanson-inc.com
1006 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:01 | Mar 14, 2018 @ 16:02 | mcoalson@hanson-inc.com
1009 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:02 | Mar 14, 2018 @ 16:02 | mcoalson@hanson-inc.com
1018 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:03 | mcoalson@hanson-inc.com
1020 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:03 | mcoalson@hanson-inc.com
1022 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:03 | mcoalson@hanson-inc.com
1031 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:05 | Mar 14, 2018 @ 16:05 | mcoalson@hanson-inc.com
1032 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:05 | Mar 14, 2018 @ 16:05 | mcoalson@hanson-inc.com
1033 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:05 | Mar 14, 2018 @ 16:05 | mcoalson@hanson-inc.com
1064 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:23 | Mar 14, 2018 @ 16:23 | nboyd@hanson-inc.com
1080 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:27 | Mar 14, 2018 @ 16:27 | mcoalson@hanson-inc.com
1083 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:27 | Mar 14, 2018 @ 16:27 | mcoalson@hanson-inc.com
662 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:20 | Mar 14, 2018 @ 13:20 | nboyd@hanson-inc.com
663 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:20 | Mar 14, 2018 @ 13:20 | nboyd@hanson-inc.com
672 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:23 | Mar 14, 2018 @ 13:23 | mcoalson@hanson-inc.com
674 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:24 | Mar 14, 2018 @ 13:24 | mcoalson@hanson-inc.com
675 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:24 | Mar 14, 2018 @ 13:24 | mcoalson@hanson-inc.com
683 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:26 | Mar 14, 2018 @ 13:26 | mcoalson@hanson-inc.com
684 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:26 | Mar 14, 2018 @ 13:26 | mcoalson@hanson-inc.com
693 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:27 | Mar 14, 2018 @ 13:27 | nboyd@hanson-inc.com
700 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:29 | Mar 14, 2018 @ 13:29 | nboyd@hanson-inc.com
702 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:29 | Mar 14, 2018 @ 13:29 | nboyd@hanson-inc.com
707 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:31 | Mar 14, 2018 @ 13:31 | nboyd@hanson-inc.com
730 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:49 | Mar 14, 2018 @ 13:49 | mcoalson@hanson-inc.com
740 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:58 | Mar 14, 2018 @ 13:58 | mcoalson@hanson-inc.com
758 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:14 | Mar 14, 2018 @ 14:14 | mcoalson@hanson-inc.com
759 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:14 | Mar 14, 2018 @ 14:14 | mcoalson@hanson-inc.com
760 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:14 | Mar 14, 2018 @ 14:14 | mcoalson@hanson-inc.com
762 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:14 | Mar 14, 2018 @ 14:14 | mcoalson@hanson-inc.com
767 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:22 | Mar 14, 2018 @ 14:16 | mcoalson@hanson-inc.com
770 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:24 | Mar 14, 2018 @ 14:18 | mcoalson@hanson-inc.com
774 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:18 | Mar 14, 2018 @ 14:18 | mcoalson@hanson-inc.com
775 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:18 | Mar 14, 2018 @ 14:18 | mcoalson@hanson-inc.com
789 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:32 | Mar 14, 2018 @ 14:32 | mcoalson@hanson-inc.com
799 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:39 | Mar 14, 2018 @ 14:39 | mcoalson@hanson-inc.com
815 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:51 | Mar 14, 2018 @ 14:44 | mcoalson@hanson-inc.com
841 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:54 | Mar 14, 2018 @ 14:54 | nboyd@hanson-inc.com
842 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:54 | Mar 14, 2018 @ 14:54 | nboyd@hanson-inc.com
845 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:54 | Mar 14, 2018 @ 14:54 | mcoalson@hanson-inc.com
846 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:54 | Mar 14, 2018 @ 14:54 | mcoalson@hanson-inc.com
854 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 15:02 | Mar 14, 2018 @ 14:56 | mcoalson@hanson-inc.com
859 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:57 | mcoalson@hanson-inc.com
860 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:57 | nboyd@hanson-inc.com
868 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 15:04 | Mar 14, 2018 @ 14:58 | mcoalson@hanson-inc.com
869 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 15:05 | Mar 14, 2018 @ 14:58 | mcoalson@hanson-inc.com
1074 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 15:02 | Mar 14, 2018 @ 16:25 | mcoalson@hanson-inc.com
20 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:11 | Mar 12, 2018 @ 14:05 | mcoalson@hanson-inc.com
22 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:05 | Mar 12, 2018 @ 14:05 | nboyd@hanson-inc.com
34 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:08 | Mar 12, 2018 @ 14:08 | nboyd@hanson-inc.com
38 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:15 | Mar 12, 2018 @ 14:09 | mcoalson@hanson-inc.com
64 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:19 | Mar 12, 2018 @ 14:19 | nboyd@hanson-inc.com
68 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:27 | Mar 12, 2018 @ 14:20 | mcoalson@hanson-inc.com
71 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:28 | Mar 12, 2018 @ 14:22 | mcoalson@hanson-inc.com
72 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:28 | Mar 12, 2018 @ 14:22 | mcoalson@hanson-inc.com
76 | M | Monitor | Ipad | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:23 | Mar 12, 2018 @ 14:23 | nboyd@hanson-inc.com
83 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:24 | Mar 12, 2018 @ 14:24 | nboyd@hanson-inc.com
91 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:33 | Mar 12, 2018 @ 14:27 | mcoalson@hanson-inc.com
94 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:35 | Mar 12, 2018 @ 14:28 | mcoalson@hanson-inc.com
95 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:35 | Mar 12, 2018 @ 14:28 | mcoalson@hanson-inc.com
102 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:29 | Mar 12, 2018 @ 14:29 | nboyd@hanson-inc.com
108 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:30 | Mar 12, 2018 @ 14:30 | nboyd@hanson-inc.com
121 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:32 | Mar 12, 2018 @ 14:32 | nboyd@hanson-inc.com
122 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:38 | Mar 12, 2018 @ 14:32 | mcoalson@hanson-inc.com
129 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:33 | Mar 12, 2018 @ 14:33 | nboyd@hanson-inc.com
139 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:42 | Mar 12, 2018 @ 14:35 | mcoalson@hanson-inc.com
140 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:35 | Mar 12, 2018 @ 14:35 | nboyd@hanson-inc.com
149 | M | Monitor | On | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:37 | Mar 12, 2018 @ 14:37 | nboyd@hanson-inc.com
159 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:45 | Mar 12, 2018 @ 14:38 | mcoalson@hanson-inc.com
165 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:46 | Mar 12, 2018 @ 14:39 | mcoalson@hanson-inc.com
169 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:40 | Mar 12, 2018 @ 14:40 | nboyd@hanson-inc.com
178 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:50 | Mar 12, 2018 @ 14:43 | mcoalson@hanson-inc.com
182 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:44 | Mar 12, 2018 @ 14:44 | nboyd@hanson-inc.com
183 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:51 | Mar 12, 2018 @ 14:45 | mcoalson@hanson-inc.com
184 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:51 | Mar 12, 2018 @ 14:45 | mcoalson@hanson-inc.com
195 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:53 | Mar 12, 2018 @ 14:47 | mcoalson@hanson-inc.com
197 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:47 | Mar 12, 2018 @ 14:47 | nboyd@hanson-inc.com
211 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:49 | Mar 12, 2018 @ 14:49 | nboyd@hanson-inc.com
220 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:57 | Mar 12, 2018 @ 14:51 | mcoalson@hanson-inc.com
221 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:51 | Mar 12, 2018 @ 14:51 | nboyd@hanson-inc.com
222 | M | Monitor | Ipad | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:51 | Mar 12, 2018 @ 14:51 | nboyd@hanson-inc.com
234 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:00 | Mar 12, 2018 @ 14:53 | mcoalson@hanson-inc.com
235 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:00 | Mar 12, 2018 @ 14:54 | mcoalson@hanson-inc.com
248 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:06 | Mar 12, 2018 @ 15:06 | nboyd@hanson-inc.com
249 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:06 | Mar 12, 2018 @ 15:06 | nboyd@hanson-inc.com
268 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:20 | Mar 12, 2018 @ 15:14 | mcoalson@hanson-inc.com
269 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:20 | Mar 12, 2018 @ 15:14 | mcoalson@hanson-inc.com
273 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:14 | Mar 12, 2018 @ 15:14 | nboyd@hanson-inc.com
278 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:23 | Mar 12, 2018 @ 15:16 | mcoalson@hanson-inc.com
282 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:24 | Mar 12, 2018 @ 15:18 | mcoalson@hanson-inc.com
290 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:26 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
291 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:26 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
889 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:10 | Mar 14, 2018 @ 15:10 | nboyd@hanson-inc.com
911 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:18 | Mar 14, 2018 @ 15:19 | nboyd@hanson-inc.com
917 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:22 | Mar 14, 2018 @ 15:22 | nboyd@hanson-inc.com
919 | LC | Lighting controls | Hall lights timer |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 2 | #N/A | Mar 14, 2018 @ 15:23 | Mar 14, 2018 @ 15:24 | nboyd@hanson-inc.com
932 | LC | Lighting controls | Toddle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:45 | Mar 14, 2018 @ 15:39 | mcoalson@hanson-inc.com
942 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:50 | Mar 14, 2018 @ 15:50 | nboyd@hanson-inc.com
957 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:52 | Mar 14, 2018 @ 15:52 | nboyd@hanson-inc.com
975 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:55 | Mar 14, 2018 @ 15:55 | nboyd@hanson-inc.com
989 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:58 | Mar 14, 2018 @ 15:58 | nboyd@hanson-inc.com
1004 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:01 | Mar 14, 2018 @ 16:01 | nboyd@hanson-inc.com
1049 | LC | Lighting controls | Occ sensor |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:15 | Mar 14, 2018 @ 16:15 | mcoalson@hanson-inc.com
1070 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:25 | Mar 14, 2018 @ 16:25 | nboyd@hanson-inc.com
634 | LC | Lighting controls | Crestron lighting control panel |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 1 | #N/A | Mar 12, 2018 @ 19:41 | Mar 12, 2018 @ 19:41 | nboyd@hanson-inc.com
637 | LC | Lighting controls | 8 pir occ sensors |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 12, 2018 @ 19:44 | Mar 12, 2018 @ 19:44 | nboyd@hanson-inc.com
638 | LC | Lighting controls | 2 dual mode occ sensors |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 12, 2018 @ 19:44 | Mar 12, 2018 @ 19:45 | nboyd@hanson-inc.com
641 | LC | Lighting controls | Occ sensor |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 12, 2018 @ 19:52 | Mar 12, 2018 @ 19:46 | mcoalson@hanson-inc.com
644 | LC | Lighting controls | Occ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 12, 2018 @ 19:49 | Mar 12, 2018 @ 19:49 | nboyd@hanson-inc.com
649 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:09 | Mar 14, 2018 @ 13:02 | mcoalson@hanson-inc.com
654 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:18 | Mar 14, 2018 @ 13:18 | nboyd@hanson-inc.com
660 | LC | Lighting controls | Switc |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:19 | Mar 14, 2018 @ 13:20 | nboyd@hanson-inc.com
688 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:26 | Mar 14, 2018 @ 13:26 | nboyd@hanson-inc.com
698 | LC | Lighting controls | Tstat |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:29 | Mar 14, 2018 @ 13:29 | nboyd@hanson-inc.com
704 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:30 | Mar 14, 2018 @ 13:31 | nboyd@hanson-inc.com
721 | LC | Lighting controls | Occ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:46 | Mar 14, 2018 @ 13:46 | nboyd@hanson-inc.com
724 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:47 | Mar 14, 2018 @ 13:47 | nboyd@hanson-inc.com
731 | LC | Lighting controls | Occ |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 13:56 | Mar 14, 2018 @ 13:50 | mcoalson@hanson-inc.com
736 | LC | Lighting controls | Lutron controls GRAFIK Eye |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 1 | #N/A | Mar 14, 2018 @ 13:56 | Mar 14, 2018 @ 13:58 | nboyd@hanson-inc.com
751 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:16 | Mar 14, 2018 @ 14:09 | mcoalson@hanson-inc.com
754 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:13 | Mar 14, 2018 @ 14:14 | nboyd@hanson-inc.com
795 | LC | Lighting controls | Toddle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:45 | Mar 14, 2018 @ 14:40 | mcoalson@hanson-inc.com
801 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:39 | Mar 14, 2018 @ 14:40 | nboyd@hanson-inc.com
838 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:53 | Mar 14, 2018 @ 14:53 | nboyd@hanson-inc.com
852 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:56 | Mar 14, 2018 @ 14:56 | nboyd@hanson-inc.com
871 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:58 | Mar 14, 2018 @ 14:59 | nboyd@hanson-inc.com
7 | LC | Lighting controls | Single switch, far side from elevator, no occ sensor. Unsafe. No emergency lights |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | M401 | 0 | #N/A | Mar 12, 2018 @ 13:42 | Mar 12, 2018 @ 13:43 | nboyd@hanson-inc.com
27 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:07 | Mar 12, 2018 @ 14:07 | nboyd@hanson-inc.com
28 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:07 | Mar 12, 2018 @ 14:07 | nboyd@hanson-inc.com
30 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:14 | Mar 12, 2018 @ 14:08 | mcoalson@hanson-inc.com
36 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:09 | Mar 12, 2018 @ 14:09 | nboyd@hanson-inc.com
49 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:18 | Mar 12, 2018 @ 14:12 | mcoalson@hanson-inc.com
50 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:12 | Mar 12, 2018 @ 14:12 | nboyd@hanson-inc.com
52 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:19 | Mar 12, 2018 @ 14:12 | mcoalson@hanson-inc.com
59 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:18 | Mar 12, 2018 @ 14:18 | nboyd@hanson-inc.com
66 | LC | Lighting controls | Switch, storage usually off |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:20 | Mar 12, 2018 @ 14:21 | nboyd@hanson-inc.com
73 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:22 | Mar 12, 2018 @ 14:22 | nboyd@hanson-inc.com
84 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:31 | Mar 12, 2018 @ 14:25 | mcoalson@hanson-inc.com
85 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:31 | Mar 12, 2018 @ 14:25 | mcoalson@hanson-inc.com
87 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:33 | Mar 12, 2018 @ 14:26 | mcoalson@hanson-inc.com
88 | LC | Lighting controls | Switch, storage usually off |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:26 | Mar 12, 2018 @ 14:27 | nboyd@hanson-inc.com
93 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:28 | Mar 12, 2018 @ 14:28 | nboyd@hanson-inc.com
103 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:36 | Mar 12, 2018 @ 14:29 | mcoalson@hanson-inc.com
104 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:29 | Mar 12, 2018 @ 14:30 | nboyd@hanson-inc.com
111 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:37 | Mar 12, 2018 @ 14:31 | mcoalson@hanson-inc.com
112 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:31 | Mar 12, 2018 @ 14:31 | nboyd@hanson-inc.com
126 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:33 | Mar 12, 2018 @ 14:33 | nboyd@hanson-inc.com
131 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:40 | Mar 12, 2018 @ 14:34 | mcoalson@hanson-inc.com
133 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:41 | Mar 12, 2018 @ 14:34 | mcoalson@hanson-inc.com
134 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:34 | Mar 12, 2018 @ 14:34 | nboyd@hanson-inc.com
143 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:42 | Mar 12, 2018 @ 14:36 | mcoalson@hanson-inc.com
145 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:36 | Mar 12, 2018 @ 14:36 | nboyd@hanson-inc.com
154 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:44 | Mar 12, 2018 @ 14:38 | mcoalson@hanson-inc.com
156 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:38 | Mar 12, 2018 @ 14:38 | nboyd@hanson-inc.com
163 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:46 | Mar 12, 2018 @ 14:39 | mcoalson@hanson-inc.com
172 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:42 | Mar 12, 2018 @ 14:42 | nboyd@hanson-inc.com
176 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:50 | Mar 12, 2018 @ 14:43 | mcoalson@hanson-inc.com
189 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:45 | Mar 12, 2018 @ 14:45 | nboyd@hanson-inc.com
190 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:52 | Mar 12, 2018 @ 14:45 | mcoalson@hanson-inc.com
191 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:52 | Mar 12, 2018 @ 14:46 | mcoalson@hanson-inc.com
201 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:54 | Mar 12, 2018 @ 14:48 | mcoalson@hanson-inc.com
202 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:48 | Mar 12, 2018 @ 14:48 | nboyd@hanson-inc.com
212 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:56 | Mar 12, 2018 @ 14:49 | mcoalson@hanson-inc.com
215 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:50 | Mar 12, 2018 @ 14:50 | nboyd@hanson-inc.com
241 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 14:59 | Mar 12, 2018 @ 14:59 | nboyd@hanson-inc.com
244 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:03 | Mar 12, 2018 @ 15:03 | nboyd@hanson-inc.com
256 | LC | Lighting controls | Occ sensor |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:14 | Mar 12, 2018 @ 15:07 | mcoalson@hanson-inc.com
257 | LC | Lighting controls | Occ sensor |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:14 | Mar 12, 2018 @ 15:07 | mcoalson@hanson-inc.com
258 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:07 | Mar 12, 2018 @ 15:08 | nboyd@hanson-inc.com
261 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:19 | Mar 12, 2018 @ 15:12 | mcoalson@hanson-inc.com
262 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:12 | Mar 12, 2018 @ 15:13 | nboyd@hanson-inc.com
280 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:24 | Mar 12, 2018 @ 15:17 | mcoalson@hanson-inc.com
281 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:24 | Mar 12, 2018 @ 15:18 | mcoalson@hanson-inc.com
301 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:31 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
311 | LC | Lighting controls | Occ sensor |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:36 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
314 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:39 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
317 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:40 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
320 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:41 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
325 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:42 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
334 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:45 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
347 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:51 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
348 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:51 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
350 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:51 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
355 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:52 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
362 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:54 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
364 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:55 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
383 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:39 | Mar 12, 2018 @ 18:33 | mcoalson@hanson-inc.com
388 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:41 | Mar 12, 2018 @ 18:35 | mcoalson@hanson-inc.com
394 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:36 | Mar 12, 2018 @ 18:36 | nboyd@hanson-inc.com
396 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:43 | Mar 12, 2018 @ 18:36 | mcoalson@hanson-inc.com
407 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:44 | Mar 12, 2018 @ 18:37 | mcoalson@hanson-inc.com
427 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:42 | Mar 12, 2018 @ 18:42 | nboyd@hanson-inc.com
439 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:00 | Mar 12, 2018 @ 18:53 | mcoalson@hanson-inc.com
442 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:54 | Mar 12, 2018 @ 18:54 | nboyd@hanson-inc.com
450 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:02 | Mar 12, 2018 @ 18:56 | mcoalson@hanson-inc.com
462 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 18:58 | Mar 12, 2018 @ 18:59 | nboyd@hanson-inc.com
463 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:05 | Mar 12, 2018 @ 18:59 | mcoalson@hanson-inc.com
469 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:07 | Mar 12, 2018 @ 19:00 | mcoalson@hanson-inc.com
475 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:01 | Mar 12, 2018 @ 19:02 | nboyd@hanson-inc.com
477 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:08 | Mar 12, 2018 @ 19:02 | mcoalson@hanson-inc.com
495 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:10 | Mar 12, 2018 @ 19:04 | mcoalson@hanson-inc.com
497 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:04 | Mar 12, 2018 @ 19:04 | nboyd@hanson-inc.com
506 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:11 | Mar 12, 2018 @ 19:05 | mcoalson@hanson-inc.com
517 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:12 | Mar 12, 2018 @ 19:06 | mcoalson@hanson-inc.com
519 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:07 | Mar 12, 2018 @ 19:07 | nboyd@hanson-inc.com
522 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:14 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
536 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:09 | Mar 12, 2018 @ 19:09 | nboyd@hanson-inc.com
539 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:09 | mcoalson@hanson-inc.com
557 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:17 | Mar 12, 2018 @ 19:11 | mcoalson@hanson-inc.com
561 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:12 | Mar 12, 2018 @ 19:12 | nboyd@hanson-inc.com
570 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:19 | Mar 12, 2018 @ 19:13 | mcoalson@hanson-inc.com
585 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:15 | nboyd@hanson-inc.com
586 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:21 | Mar 12, 2018 @ 19:15 | mcoalson@hanson-inc.com
595 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:22 | Mar 12, 2018 @ 19:16 | mcoalson@hanson-inc.com
604 | LC | Lighting controls | Toggle |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:23 | Mar 12, 2018 @ 19:17 | mcoalson@hanson-inc.com
611 | LC | Lighting controls | Switch |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 19:17 | Mar 12, 2018 @ 19:17 | nboyd@hanson-inc.com
299 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:30 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
322 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:42 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
328 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:43 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
329 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:43 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
336 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:46 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
341 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:47 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
344 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:50 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
345 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:50 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
352 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:51 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
357 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:53 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
358 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:53 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
367 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:55 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
375 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:57 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
376 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:57 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
377 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:58 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
378 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:58 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
389 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:41 | Mar 12, 2018 @ 18:35 | mcoalson@hanson-inc.com
390 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:41 | Mar 12, 2018 @ 18:35 | mcoalson@hanson-inc.com
401 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:43 | Mar 12, 2018 @ 18:36 | mcoalson@hanson-inc.com
408 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:44 | Mar 12, 2018 @ 18:37 | mcoalson@hanson-inc.com
418 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:40 | Mar 12, 2018 @ 18:40 | nboyd@hanson-inc.com
419 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:47 | Mar 12, 2018 @ 18:41 | mcoalson@hanson-inc.com
447 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:55 | Mar 12, 2018 @ 18:55 | nboyd@hanson-inc.com
448 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:56 | Mar 12, 2018 @ 18:56 | nboyd@hanson-inc.com
458 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:04 | Mar 12, 2018 @ 18:57 | mcoalson@hanson-inc.com
459 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:04 | Mar 12, 2018 @ 18:58 | mcoalson@hanson-inc.com
468 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:00 | Mar 12, 2018 @ 19:00 | nboyd@hanson-inc.com
474 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:07 | Mar 12, 2018 @ 19:01 | mcoalson@hanson-inc.com
481 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:02 | Mar 12, 2018 @ 19:02 | nboyd@hanson-inc.com
482 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:09 | Mar 12, 2018 @ 19:02 | mcoalson@hanson-inc.com
483 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:02 | Mar 12, 2018 @ 19:02 | nboyd@hanson-inc.com
491 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:10 | Mar 12, 2018 @ 19:04 | mcoalson@hanson-inc.com
496 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:10 | Mar 12, 2018 @ 19:04 | mcoalson@hanson-inc.com
501 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:11 | Mar 12, 2018 @ 19:05 | mcoalson@hanson-inc.com
505 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:05 | Mar 12, 2018 @ 19:05 | nboyd@hanson-inc.com
507 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:05 | Mar 12, 2018 @ 19:05 | nboyd@hanson-inc.com
509 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:12 | Mar 12, 2018 @ 19:05 | mcoalson@hanson-inc.com
513 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:12 | Mar 12, 2018 @ 19:06 | mcoalson@hanson-inc.com
527 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:14 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
532 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:08 | Mar 12, 2018 @ 19:08 | nboyd@hanson-inc.com
533 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:08 | Mar 12, 2018 @ 19:08 | nboyd@hanson-inc.com
535 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
543 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:09 | mcoalson@hanson-inc.com
546 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:16 | Mar 12, 2018 @ 19:09 | mcoalson@hanson-inc.com
547 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:10 | Mar 12, 2018 @ 19:10 | nboyd@hanson-inc.com
548 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:10 | Mar 12, 2018 @ 19:10 | nboyd@hanson-inc.com
551 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:17 | Mar 12, 2018 @ 19:11 | mcoalson@hanson-inc.com
553 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:17 | Mar 12, 2018 @ 19:11 | mcoalson@hanson-inc.com
560 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:18 | Mar 12, 2018 @ 19:12 | mcoalson@hanson-inc.com
563 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:19 | Mar 12, 2018 @ 19:13 | mcoalson@hanson-inc.com
566 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:19 | Mar 12, 2018 @ 19:13 | mcoalson@hanson-inc.com
573 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:20 | Mar 12, 2018 @ 19:13 | mcoalson@hanson-inc.com
574 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:20 | Mar 12, 2018 @ 19:13 | mcoalson@hanson-inc.com
575 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:13 | Mar 12, 2018 @ 19:13 | nboyd@hanson-inc.com
576 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:13 | Mar 12, 2018 @ 19:13 | nboyd@hanson-inc.com
916 | M | Mechanical | Very cold in 105 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 15:20 | Mar 14, 2018 @ 15:21 | nboyd@hanson-inc.com
579 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:21 | Mar 12, 2018 @ 19:14 | mcoalson@hanson-inc.com
1072 | M | Mechanical | Dirty SA vent. |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 1 | #N/A | Mar 14, 2018 @ 16:25 | Mar 14, 2018 @ 16:26 | mcoalson@hanson-inc.com
1098 | M | Mechanical | Air separator |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 1 | #N/A | Mar 14, 2018 @ 17:41 | Mar 14, 2018 @ 17:42 | mcoalson@hanson-inc.com
743 | M | Mechanical | Dirty supply grills |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 1 | #N/A | Mar 14, 2018 @ 14:01 | Mar 14, 2018 @ 14:01 | nboyd@hanson-inc.com
804 | M | Mechanical | Need to clean return |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 1 | #N/A | Mar 14, 2018 @ 14:41 | Mar 14, 2018 @ 14:43 | mcoalson@hanson-inc.com
848 | M | Mechanical | Mechanical hvac hum above ceiling room 223 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:54 | Mar 14, 2018 @ 14:55 | nboyd@hanson-inc.com
436 | M | Mechanical | Dirty supply diffusers, a lot of air movement |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 1 | #N/A | Mar 12, 2018 @ 18:47 | Mar 12, 2018 @ 18:49 | nboyd@hanson-inc.com
581 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:21 | Mar 12, 2018 @ 19:15 | mcoalson@hanson-inc.com
590 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:15 | nboyd@hanson-inc.com
591 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:15 | nboyd@hanson-inc.com
592 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:15 | nboyd@hanson-inc.com
600 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:22 | Mar 12, 2018 @ 19:16 | mcoalson@hanson-inc.com
608 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:23 | Mar 12, 2018 @ 19:17 | mcoalson@hanson-inc.com
610 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:23 | Mar 12, 2018 @ 19:17 | mcoalson@hanson-inc.com
616 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:18 | Mar 12, 2018 @ 19:18 | nboyd@hanson-inc.com
617 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:18 | Mar 12, 2018 @ 19:18 | nboyd@hanson-inc.com
621 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:28 | Mar 12, 2018 @ 19:21 | mcoalson@hanson-inc.com
623 | M | Monitor |  | 21 | 1 | 100% | 21 | 114.975 | 12.2579 | 0.0018908 | 392.311 | 0.0064515 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:28 | Mar 12, 2018 @ 19:22 | mcoalson@hanson-inc.com
964 | HT | Personal heater | 1500w | 1500 | 1 | 20% | 1500 | 1642.5 | 175.1124 | 0.027011 | 5604.4426 | 0.092165 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:53 | Mar 14, 2018 @ 15:53 | nboyd@hanson-inc.com
1024 | HT | Personal heater | 1200w | 1200 | 1 | 20% | 1200 | 1314 | 140.0899 | 0.021609 | 4483.5541 | 0.073732 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:04 | Mar 14, 2018 @ 16:04 | nboyd@hanson-inc.com
1085 | HT | Personal heater |  | 1350 | 1 | 20% | 1350 | 1478.25 | 157.6012 | 0.02431 | 5043.9984 | 0.082948 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:28 | Mar 14, 2018 @ 16:28 | mcoalson@hanson-inc.com
1087 | HT | Personal heater | 1500w | 1500 | 1 | 20% | 1500 | 1642.5 | 175.1124 | 0.027011 | 5604.4426 | 0.092165 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:28 | Mar 14, 2018 @ 16:29 | nboyd@hanson-inc.com
682 | HT | Personal heater | 1500w | 1500 | 1 | 20% | 1500 | 1642.5 | 175.1124 | 0.027011 | 5604.4426 | 0.092165 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:25 | Mar 14, 2018 @ 13:25 | nboyd@hanson-inc.com
849 | HT | Personal heater |  | 1350 | 1 | 20% | 1350 | 1478.25 | 157.6012 | 0.02431 | 5043.9984 | 0.082948 | 2nd Floor | 1 | Plug Load | Mar 14, 2018 @ 14:54 | Mar 14, 2018 @ 14:55 | mcoalson@hanson-inc.com
58 | HT | Personal heater | 1500w | 1500 | 1 | 20% | 1500 | 1642.5 | 175.1124 | 0.027011 | 5604.4426 | 0.092165 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:13 | Mar 12, 2018 @ 14:14 | nboyd@hanson-inc.com
277 | HT | Personal heater | 1500w | 1500 | 1 | 20% | 1500 | 1642.5 | 175.1124 | 0.027011 | 5604.4426 | 0.092165 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:16 | Mar 12, 2018 @ 15:16 | nboyd@hanson-inc.com
510 | HT | Personal heater | 200w | 200 | 1 | 20% | 200 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:05 | Mar 12, 2018 @ 19:06 | nboyd@hanson-inc.com
687 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:26 | Mar 14, 2018 @ 13:26 | mcoalson@hanson-inc.com
764 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:15 | Mar 14, 2018 @ 14:15 | mcoalson@hanson-inc.com
779 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:19 | Mar 14, 2018 @ 14:19 | mcoalson@hanson-inc.com
914 | MS | Miscellaneous | Coin machine |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 1 | #N/A | Mar 14, 2018 @ 15:20 | Mar 14, 2018 @ 15:20 | nboyd@hanson-inc.com
939 | MS | Miscellaneous |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 2 | #N/A | Mar 14, 2018 @ 15:47 | Mar 14, 2018 @ 15:48 | mcoalson@hanson-inc.com
782 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:22 | Mar 14, 2018 @ 14:22 | mcoalson@hanson-inc.com
847 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:54 | Mar 14, 2018 @ 14:54 | mcoalson@hanson-inc.com
861 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:57 | mcoalson@hanson-inc.com
23 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:12 | Mar 12, 2018 @ 14:05 | mcoalson@hanson-inc.com
1101 | MS | Miscellaneous | VFD - note the motor overload is in alarm. |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 2 | #N/A | Mar 14, 2018 @ 17:44 | Mar 14, 2018 @ 17:45 | mcoalson@hanson-inc.com
1103 | MS | Miscellaneous | VFD |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 2 | #N/A | Mar 14, 2018 @ 17:45 | Mar 14, 2018 @ 17:46 | mcoalson@hanson-inc.com
1104 | MS | Miscellaneous | Expansion tank with both valves closed. |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 1 | #N/A | Mar 14, 2018 @ 17:57 | Mar 14, 2018 @ 19:36 | mcoalson@hanson-inc.com
1105 | MS | Miscellaneous | Temp: 70.2 CO2 492 RH 33.9% |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 16, 2018 @ 15:35 | Mar 16, 2018 @ 15:37 | mcoalson@hanson-inc.com
1106 | MS | Miscellaneous | Temp 70.1 CO2 540 RH 34% |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 16, 2018 @ 15:43 | Mar 16, 2018 @ 15:45 | mcoalson@hanson-inc.com
40 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:16 | Mar 12, 2018 @ 14:09 | mcoalson@hanson-inc.com
46 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:17 | Mar 12, 2018 @ 14:11 | mcoalson@hanson-inc.com
56 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:19 | Mar 12, 2018 @ 14:13 | mcoalson@hanson-inc.com
86 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:32 | Mar 12, 2018 @ 14:25 | mcoalson@hanson-inc.com
96 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:35 | Mar 12, 2018 @ 14:28 | mcoalson@hanson-inc.com
742 | MS | Miscellaneous | Classroom controls |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 2 | #N/A | Mar 14, 2018 @ 14:00 | Mar 14, 2018 @ 14:04 | mcoalson@hanson-inc.com
788 | MS | Miscellaneous | Classroom controls |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:32 | Mar 14, 2018 @ 14:32 | mcoalson@hanson-inc.com
123 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:38 | Mar 12, 2018 @ 14:32 | mcoalson@hanson-inc.com
135 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:41 | Mar 12, 2018 @ 14:34 | mcoalson@hanson-inc.com
800 | MS | Miscellaneous | Classroom controls |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 14, 2018 @ 14:39 | Mar 14, 2018 @ 14:39 | mcoalson@hanson-inc.com
157 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:45 | Mar 12, 2018 @ 14:38 | mcoalson@hanson-inc.com
180 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:50 | Mar 12, 2018 @ 14:44 | mcoalson@hanson-inc.com
1107 | MS | Miscellaneous | Temp 70 CO2 527 RH 33% |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 16, 2018 @ 15:46 | Mar 16, 2018 @ 15:56 | mcoalson@hanson-inc.com
1108 | MS | Miscellaneous | Temp 71 CO2 458 RH 35% |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 0 | #N/A | Mar 16, 2018 @ 15:56 | Mar 16, 2018 @ 15:57 | mcoalson@hanson-inc.com
188 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:52 | Mar 12, 2018 @ 14:45 | mcoalson@hanson-inc.com
194 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:53 | Mar 12, 2018 @ 14:46 | mcoalson@hanson-inc.com
217 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:57 | Mar 12, 2018 @ 14:50 | mcoalson@hanson-inc.com
319 | MS | Miscellaneous | Fan is making a lot of noise in this room. |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 12, 2018 @ 15:40 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
272 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:20 | Mar 12, 2018 @ 15:14 | mcoalson@hanson-inc.com
1109 | MS | Miscellaneous | Temp 68 CO2 464 RH 33% |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 16, 2018 @ 16:07 | Mar 16, 2018 @ 16:11 | mcoalson@hanson-inc.com
1110 | MS | Miscellaneous | Temp 69 CO2 457 RH 33% |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | VTU3-20 | 0 | #N/A | Mar 16, 2018 @ 16:11 | Mar 16, 2018 @ 16:15 | mcoalson@hanson-inc.com
293 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:26 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
316 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:40 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
324 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:42 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
330 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:43 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
335 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:45 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
339 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:47 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
349 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:51 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
354 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:52 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
356 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:53 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
359 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:53 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
366 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:55 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
387 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:40 | Mar 12, 2018 @ 18:34 | mcoalson@hanson-inc.com
392 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:41 | Mar 12, 2018 @ 18:35 | mcoalson@hanson-inc.com
399 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:43 | Mar 12, 2018 @ 18:36 | mcoalson@hanson-inc.com
421 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:47 | Mar 12, 2018 @ 18:41 | mcoalson@hanson-inc.com
422 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:47 | Mar 12, 2018 @ 18:41 | mcoalson@hanson-inc.com
460 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:04 | Mar 12, 2018 @ 18:58 | mcoalson@hanson-inc.com
465 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:06 | Mar 12, 2018 @ 18:59 | mcoalson@hanson-inc.com
485 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:09 | Mar 12, 2018 @ 19:02 | mcoalson@hanson-inc.com
486 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:09 | Mar 12, 2018 @ 19:03 | mcoalson@hanson-inc.com
490 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:10 | Mar 12, 2018 @ 19:04 | mcoalson@hanson-inc.com
500 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:11 | Mar 12, 2018 @ 19:05 | mcoalson@hanson-inc.com
512 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:12 | Mar 12, 2018 @ 19:06 | mcoalson@hanson-inc.com
528 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:14 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
544 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:09 | mcoalson@hanson-inc.com
552 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:17 | Mar 12, 2018 @ 19:11 | mcoalson@hanson-inc.com
565 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:19 | Mar 12, 2018 @ 19:13 | mcoalson@hanson-inc.com
580 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:21 | Mar 12, 2018 @ 19:15 | mcoalson@hanson-inc.com
601 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:22 | Mar 12, 2018 @ 19:16 | mcoalson@hanson-inc.com
609 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:23 | Mar 12, 2018 @ 19:17 | mcoalson@hanson-inc.com
622 | PH | Phone |  | 5 | 1 | 100% | 5 | 27.375 | 2.9185 | 0.00045018 | 93.4074 | 0.0015361 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:28 | Mar 12, 2018 @ 19:22 | mcoalson@hanson-inc.com
1044 | P | Plumbing | Drinking fountains | 370 | 1 | 75% | 370 | 1519.3125 | 161.979 | 0.024985 | 5184.1094 | 0.085252 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 16:13 | Mar 14, 2018 @ 16:13 | nboyd@hanson-inc.com
728 | P | Plumbing | 8kw instant hot water heater ewh-1 | 8000 | 1 | 10% | 8000 | 4380 | 466.9664 | 0.072029 | 14945.1804 | 0.24577 | 2nd Floor | 1 | DHW | Mar 14, 2018 @ 13:48 | Mar 14, 2018 @ 13:49 | nboyd@hanson-inc.com
947 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 2 | Plug Load | Mar 14, 2018 @ 15:51 | Mar 14, 2018 @ 15:51 | mcoalson@hanson-inc.com
953 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:52 | Mar 14, 2018 @ 15:52 | mcoalson@hanson-inc.com
963 | PR | Printer | MD | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 15:59 | Mar 14, 2018 @ 15:54 | mcoalson@hanson-inc.com
971 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:54 | Mar 14, 2018 @ 15:54 | mcoalson@hanson-inc.com
987 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:57 | Mar 14, 2018 @ 15:57 | mcoalson@hanson-inc.com
1025 | PR | Printer | SM | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 16:10 | Mar 14, 2018 @ 16:05 | mcoalson@hanson-inc.com
1028 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:04 | Mar 14, 2018 @ 16:04 | nboyd@hanson-inc.com
1037 | PR | Printer | SM | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:12 | Mar 14, 2018 @ 16:06 | mcoalson@hanson-inc.com
1057 | PR | Printer | SM | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:27 | Mar 14, 2018 @ 16:21 | mcoalson@hanson-inc.com
1058 | PR | Printer | Scanner | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 16:28 | Mar 14, 2018 @ 16:22 | mcoalson@hanson-inc.com
1061 | PR | Printer | LG | 700 | 1 | 10% | 700 | 383.25 | 40.8596 | 0.0063025 | 1307.7033 | 0.021505 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 16:29 | Mar 14, 2018 @ 16:23 | mcoalson@hanson-inc.com
1068 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:24 | Mar 14, 2018 @ 16:25 | mcoalson@hanson-inc.com
1081 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:27 | Mar 14, 2018 @ 16:27 | nboyd@hanson-inc.com
1082 | PR | Printer | Fax Machine | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 16:34 | Mar 14, 2018 @ 16:29 | mcoalson@hanson-inc.com
1092 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:30 | Mar 14, 2018 @ 16:30 | mcoalson@hanson-inc.com
657 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:18 | Mar 14, 2018 @ 13:18 | nboyd@hanson-inc.com
664 | PR | Printer | LG | 700 | 1 | 10% | 700 | 383.25 | 40.8596 | 0.0063025 | 1307.7033 | 0.021505 | 2nd Floor | 1 | Plug Load | Mar 14, 2018 @ 13:27 | Mar 14, 2018 @ 13:22 | mcoalson@hanson-inc.com
666 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:21 | Mar 14, 2018 @ 13:21 | nboyd@hanson-inc.com
668 | PR | Printer | MD | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 1 | Plug Load | Mar 14, 2018 @ 13:29 | Mar 14, 2018 @ 13:23 | mcoalson@hanson-inc.com
685 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:26 | Mar 14, 2018 @ 13:26 | mcoalson@hanson-inc.com
694 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:27 | Mar 14, 2018 @ 13:27 | nboyd@hanson-inc.com
778 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:19 | Mar 14, 2018 @ 14:19 | mcoalson@hanson-inc.com
783 | PR | Printer | Printer | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:22 | Mar 14, 2018 @ 14:22 | mcoalson@hanson-inc.com
850 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:55 | Mar 14, 2018 @ 14:55 | mcoalson@hanson-inc.com
863 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:57 | nboyd@hanson-inc.com
872 | PR | Printer | SM | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | 2nd Floor | 1 | Plug Load | Mar 14, 2018 @ 15:05 | Mar 14, 2018 @ 14:59 | mcoalson@hanson-inc.com
26 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:06 | Mar 12, 2018 @ 14:06 | nboyd@hanson-inc.com
31 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:08 | Mar 12, 2018 @ 14:08 | nboyd@hanson-inc.com
35 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:15 | Mar 12, 2018 @ 14:09 | mcoalson@hanson-inc.com
45 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:11 | Mar 12, 2018 @ 14:11 | nboyd@hanson-inc.com
48 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:18 | Mar 12, 2018 @ 14:11 | mcoalson@hanson-inc.com
53 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:12 | Mar 12, 2018 @ 14:12 | nboyd@hanson-inc.com
55 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:19 | Mar 12, 2018 @ 14:13 | mcoalson@hanson-inc.com
62 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:19 | Mar 12, 2018 @ 14:19 | nboyd@hanson-inc.com
74 | PR | Printer | LG | 700 | 1 | 10% | 700 | 383.25 | 40.8596 | 0.0063025 | 1307.7033 | 0.021505 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:28 | Mar 12, 2018 @ 14:22 | mcoalson@hanson-inc.com
79 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:24 | Mar 12, 2018 @ 14:24 | nboyd@hanson-inc.com
89 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:33 | Mar 12, 2018 @ 14:27 | mcoalson@hanson-inc.com
92 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:34 | Mar 12, 2018 @ 14:28 | mcoalson@hanson-inc.com
119 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:32 | Mar 12, 2018 @ 14:32 | nboyd@hanson-inc.com
120 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:38 | Mar 12, 2018 @ 14:32 | mcoalson@hanson-inc.com
130 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:34 | Mar 12, 2018 @ 14:34 | nboyd@hanson-inc.com
136 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:41 | Mar 12, 2018 @ 14:35 | mcoalson@hanson-inc.com
138 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:35 | Mar 12, 2018 @ 14:35 | nboyd@hanson-inc.com
146 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:43 | Mar 12, 2018 @ 14:36 | mcoalson@hanson-inc.com
155 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:44 | Mar 12, 2018 @ 14:38 | mcoalson@hanson-inc.com
174 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:48 | Mar 12, 2018 @ 14:42 | mcoalson@hanson-inc.com
179 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:50 | Mar 12, 2018 @ 14:43 | mcoalson@hanson-inc.com
185 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:51 | Mar 12, 2018 @ 14:45 | mcoalson@hanson-inc.com
196 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:53 | Mar 12, 2018 @ 14:47 | mcoalson@hanson-inc.com
209 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:49 | Mar 12, 2018 @ 14:49 | nboyd@hanson-inc.com
219 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:57 | Mar 12, 2018 @ 14:51 | mcoalson@hanson-inc.com
224 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:52 | Mar 12, 2018 @ 14:52 | nboyd@hanson-inc.com
237 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:00 | Mar 12, 2018 @ 14:54 | mcoalson@hanson-inc.com
251 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:06 | Mar 12, 2018 @ 15:06 | nboyd@hanson-inc.com
267 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:20 | Mar 12, 2018 @ 15:14 | mcoalson@hanson-inc.com
275 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:15 | Mar 12, 2018 @ 15:15 | nboyd@hanson-inc.com
285 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:25 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
294 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:26 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
309 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 2 | Plug Load | Mar 12, 2018 @ 15:33 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
331 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:44 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
382 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 16:00 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
410 | PR | Printer | Sm | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:44 | Mar 12, 2018 @ 18:41 | mcoalson@hanson-inc.com
415 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:40 | Mar 12, 2018 @ 18:40 | nboyd@hanson-inc.com
416 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:40 | Mar 12, 2018 @ 18:40 | nboyd@hanson-inc.com
423 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:47 | Mar 12, 2018 @ 18:41 | mcoalson@hanson-inc.com
449 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:56 | Mar 12, 2018 @ 18:56 | nboyd@hanson-inc.com
451 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:56 | Mar 12, 2018 @ 18:56 | nboyd@hanson-inc.com
453 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:56 | Mar 12, 2018 @ 18:56 | nboyd@hanson-inc.com
455 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:04 | Mar 12, 2018 @ 18:57 | mcoalson@hanson-inc.com
456 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:04 | Mar 12, 2018 @ 18:57 | mcoalson@hanson-inc.com
472 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:07 | Mar 12, 2018 @ 19:01 | mcoalson@hanson-inc.com
478 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:08 | Mar 12, 2018 @ 19:02 | mcoalson@hanson-inc.com
487 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:03 | Mar 12, 2018 @ 19:03 | nboyd@hanson-inc.com
494 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:10 | Mar 12, 2018 @ 19:04 | mcoalson@hanson-inc.com
504 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:11 | Mar 12, 2018 @ 19:05 | mcoalson@hanson-inc.com
516 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:12 | Mar 12, 2018 @ 19:06 | mcoalson@hanson-inc.com
524 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:14 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
540 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:09 | mcoalson@hanson-inc.com
556 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:17 | Mar 12, 2018 @ 19:11 | mcoalson@hanson-inc.com
571 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:13 | Mar 12, 2018 @ 19:13 | nboyd@hanson-inc.com
584 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:21 | Mar 12, 2018 @ 19:15 | mcoalson@hanson-inc.com
596 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:22 | Mar 12, 2018 @ 19:16 | mcoalson@hanson-inc.com
605 | PR | Printer | Med | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:23 | Mar 12, 2018 @ 19:17 | mcoalson@hanson-inc.com
613 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:18 | Mar 12, 2018 @ 19:18 | nboyd@hanson-inc.com
625 | PR | Printer |  | 100 | 1 | 10% | 100 | 54.75 | 5.8371 | 0.00090036 | 186.8148 | 0.0030722 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:29 | Mar 12, 2018 @ 19:23 | mcoalson@hanson-inc.com
1096 | P | Pump | Chilled water Onicaon flow and energy measurement is not reading properly. | 11185.5 | 1 | 50% | 11185.5 | 30620.3063 | 3264.5331 | 0.50355 | 104480.8218 | 1.7182 | 1st Floor | 2 | Pump | Mar 14, 2018 @ 17:39 | Mar 14, 2018 @ 17:53 | mcoalson@hanson-inc.com
1097 | P | Pump |  | 11185.5 | 1 | 50% | 11185.5 | 30620.3063 | 3264.5331 | 0.50355 | 104480.8218 | 1.7182 | 1st Floor | 1 | Pump | Mar 14, 2018 @ 17:46 | Mar 14, 2018 @ 17:40 | mcoalson@hanson-inc.com
935 | RE | Refrigerator |  | 408 | 1 | 75% | 408 | 1675.35 | 178.6147 | 0.027551 | 5716.5315 | 0.094008 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:46 | Mar 14, 2018 @ 15:46 | mcoalson@hanson-inc.com
945 | RE | Refrigerator | Mini | 100 | 1 | 75% | 100 | 410.625 | 43.7781 | 0.0067527 | 1401.1107 | 0.023041 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:50 | Mar 14, 2018 @ 15:51 | mcoalson@hanson-inc.com
1089 | RE | Refrigerator |  | 408 | 1 | 75% | 408 | 1675.35 | 178.6147 | 0.027551 | 5716.5315 | 0.094008 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 16:34 | Mar 14, 2018 @ 16:29 | mcoalson@hanson-inc.com
692 | RE | Refrigerator | Mini | 100 | 1 | 75% | 100 | 410.625 | 43.7781 | 0.0067527 | 1401.1107 | 0.023041 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:27 | Mar 14, 2018 @ 13:27 | mcoalson@hanson-inc.com
711 | RE | Refrigerator |  | 408 | 1 | 75% | 408 | 1675.35 | 178.6147 | 0.027551 | 5716.5315 | 0.094008 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:34 | Mar 14, 2018 @ 13:34 | nboyd@hanson-inc.com
870 | RE | Refrigerator |  | 408 | 1 | 75% | 408 | 1675.35 | 178.6147 | 0.027551 | 5716.5315 | 0.094008 | 2nd Floor | 1 | Plug Load | Mar 14, 2018 @ 15:05 | Mar 14, 2018 @ 14:58 | mcoalson@hanson-inc.com
82 | RE | Refrigerator | Mini | 100 | 1 | 75% | 100 | 410.625 | 43.7781 | 0.0067527 | 1401.1107 | 0.023041 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:31 | Mar 12, 2018 @ 14:24 | mcoalson@hanson-inc.com
101 | RE | Refrigerator | Mini | 100 | 1 | 75% | 100 | 410.625 | 43.7781 | 0.0067527 | 1401.1107 | 0.023041 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:35 | Mar 12, 2018 @ 14:29 | mcoalson@hanson-inc.com
305 | RE | Refrigerator | Lg | 408 | 1 | 75% | 408 | 1675.35 | 178.6147 | 0.027551 | 5716.5315 | 0.094008 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 15:33 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
381 | RE | Refrigerator | Mini | 100 | 1 | 75% | 100 | 410.625 | 43.7781 | 0.0067527 | 1401.1107 | 0.023041 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 16:00 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
400 | RE | Refrigerator |  | 408 | 1 | 75% | 408 | 1675.35 | 178.6147 | 0.027551 | 5716.5315 | 0.094008 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:36 | Mar 12, 2018 @ 18:36 | nboyd@hanson-inc.com
426 | RE | Refrigerator | Mini | 100 | 1 | 75% | 100 | 410.625 | 43.7781 | 0.0067527 | 1401.1107 | 0.023041 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:48 | Mar 12, 2018 @ 18:42 | mcoalson@hanson-inc.com
444 | RE | Refrigerator | Mini | 100 | 1 | 75% | 100 | 410.625 | 43.7781 | 0.0067527 | 1401.1107 | 0.023041 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:01 | Mar 12, 2018 @ 18:55 | mcoalson@hanson-inc.com
518 | RE | Refrigerator |  | 408 | 1 | 75% | 408 | 1675.35 | 178.6147 | 0.027551 | 5716.5315 | 0.094008 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:13 | Mar 12, 2018 @ 19:06 | mcoalson@hanson-inc.com
521 | RE | Refrigerator |  | 408 | 1 | 75% | 408 | 1675.35 | 178.6147 | 0.027551 | 5716.5315 | 0.094008 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:14 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
558 | RE | Refrigerator |  | 408 | 1 | 75% | 408 | 1675.35 | 178.6147 | 0.027551 | 5716.5315 | 0.094008 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:18 | Mar 12, 2018 @ 19:12 | mcoalson@hanson-inc.com
594 | RE | Refrigerator |  | 408 | 1 | 75% | 408 | 1675.35 | 178.6147 | 0.027551 | 5716.5315 | 0.094008 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 19:22 | Mar 12, 2018 @ 19:16 | mcoalson@hanson-inc.com
950 | SH | Shredder |  | 265 | 1 | 10% | 265 | 145.0875 | 15.4683 | 0.002386 | 495.0591 | 0.0081412 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 15:51 | Mar 14, 2018 @ 15:51 | mcoalson@hanson-inc.com
1056 | SH | Shredder |  | 265 | 1 | 10% | 265 | 145.0875 | 15.4683 | 0.002386 | 495.0591 | 0.0081412 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:27 | Mar 14, 2018 @ 16:21 | mcoalson@hanson-inc.com
1071 | SH | Shredder |  | 265 | 1 | 10% | 265 | 145.0875 | 15.4683 | 0.002386 | 495.0591 | 0.0081412 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:25 | Mar 14, 2018 @ 16:25 | mcoalson@hanson-inc.com
712 | SH | Shredder |  | 265 | 1 | 10% | 265 | 145.0875 | 15.4683 | 0.002386 | 495.0591 | 0.0081412 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 13:34 | Mar 14, 2018 @ 13:34 | nboyd@hanson-inc.com
771 | SH | Shredder |  | 265 | 1 | 10% | 265 | 145.0875 | 15.4683 | 0.002386 | 495.0591 | 0.0081412 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:24 | Mar 14, 2018 @ 14:18 | mcoalson@hanson-inc.com
876 | SH | Shredder |  | 265 | 1 | 10% | 265 | 145.0875 | 15.4683 | 0.002386 | 495.0591 | 0.0081412 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:59 | Mar 14, 2018 @ 14:59 | nboyd@hanson-inc.com
80 | SH | Shredder |  | 265 | 1 | 10% | 265 | 145.0875 | 15.4683 | 0.002386 | 495.0591 | 0.0081412 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 14:30 | Mar 12, 2018 @ 14:24 | mcoalson@hanson-inc.com
302 | SH | Shredder | Lg | 265 | 1 | 10% | 265 | 145.0875 | 15.4683 | 0.002386 | 495.0591 | 0.0081412 | VTU3-20 | 1 | Plug Load | Mar 12, 2018 @ 15:32 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
379 | SH | Shredder | Lg | 265 | 1 | 10% | 265 | 145.0875 | 15.4683 | 0.002386 | 495.0591 | 0.0081412 | VTU3-20 | 1 | Plug Load | Mar 12, 2018 @ 15:58 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
411 | SH | Shredder |  | 265 | 1 | 10% | 265 | 145.0875 | 15.4683 | 0.002386 | 495.0591 | 0.0081412 | VTU3-20 | 0 | Plug Load | Mar 12, 2018 @ 18:39 | Mar 12, 2018 @ 18:39 | nboyd@hanson-inc.com
647 | TV | Television | 41 Energy Star | 175 | 1 | 25% | 175 | 239.5312 | 25.5372 | 0.0039391 | 817.3146 | 0.013441 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 12:44 | Mar 14, 2018 @ 12:42 | mcoalson@hanson-inc.com
837 | TV | Television |  | 175 | 1 | 25% | 175 | 239.5312 | 25.5372 | 0.0039391 | 817.3146 | 0.013441 | 2nd Floor | 1 | Plug Load | Mar 14, 2018 @ 14:59 | Mar 14, 2018 @ 14:53 | mcoalson@hanson-inc.com
784 | TY | Typical Office |  | 237 | 1 | 100% | 237 | 1297.575 | 138.3388 | 0.021339 | 4427.5097 | 0.07281 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:37 | Mar 14, 2018 @ 14:31 | mcoalson@hanson-inc.com
785 | TY | Typical Office |  | 237 | 1 | 100% | 237 | 1297.575 | 138.3388 | 0.021339 | 4427.5097 | 0.07281 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:37 | Mar 14, 2018 @ 14:31 | mcoalson@hanson-inc.com
786 | TY | Typical Office |  | 237 | 1 | 100% | 237 | 1297.575 | 138.3388 | 0.021339 | 4427.5097 | 0.07281 | 2nd Floor | 0 | Plug Load | Mar 14, 2018 @ 14:37 | Mar 14, 2018 @ 14:31 | mcoalson@hanson-inc.com
1090 | WH | Water Heater | Water Cooler | 370 | 1 | 75% | 370 | 1519.3125 | 161.979 | 0.024985 | 5184.1094 | 0.085252 | 1st Floor | 1 | Plug Load | Mar 14, 2018 @ 16:35 | Mar 14, 2018 @ 16:29 | mcoalson@hanson-inc.com
761 | WH | Water Heater | Water heater and cooler | 370 | 1 | 75% | 370 | 1519.3125 | 161.979 | 0.024985 | 5184.1094 | 0.085252 | 2nd Floor | 1 | Plug Load | Mar 14, 2018 @ 14:14 | Mar 14, 2018 @ 14:16 | nboyd@hanson-inc.com
| VAV |  |  | 5000 | 1 | 2% | 5000 | 547.5 | 58.3708 | 0.0090036 | 1868.1475 | 0.030722 |  |  | Heating
| VAV |  |  | 1000 | 1 | 2% | 1000 | 109.5 | 11.6742 | 0.0018007 | 373.6295 | 0.0061443 |  |  | Heating
| VAV |  |  | 6000 | 1 | 2% | 6000 | 657 | 70.045 | 0.010804 | 2241.7771 | 0.036866 |  |  | Heating
| VAV |  |  | 19000 | 1 | 2% | 19000 | 2080.5 | 221.8091 | 0.034214 | 7098.9607 | 0.11674 |  |  | Heating
| VAV |  |  | 11000 | 1 | 2% | 11000 | 1204.5 | 128.4158 | 0.019808 | 4109.9246 | 0.067587 |  |  | Heating
| VAV |  |  | 11000 | 1 | 2% | 11000 | 1204.5 | 128.4158 | 0.019808 | 4109.9246 | 0.067587 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 1000 | 1 | 2% | 1000 | 109.5 | 11.6742 | 0.0018007 | 373.6295 | 0.0061443 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 1000 | 1 | 2% | 1000 | 109.5 | 11.6742 | 0.0018007 | 373.6295 | 0.0061443 |  |  | Heating
| VAV |  |  | 7000 | 1 | 2% | 7000 | 766.5 | 81.7191 | 0.012605 | 2615.4066 | 0.04301 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 5000 | 1 | 2% | 5000 | 547.5 | 58.3708 | 0.0090036 | 1868.1475 | 0.030722 |  |  | Heating
| VAV |  |  | 2500 | 1 | 2% | 2500 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 |  |  | Heating
| VAV |  |  | 6000 | 1 | 2% | 6000 | 657 | 70.045 | 0.010804 | 2241.7771 | 0.036866 |  |  | Heating
| VAV |  |  | 6000 | 1 | 2% | 6000 | 657 | 70.045 | 0.010804 | 2241.7771 | 0.036866 |  |  | Heating
| VAV |  |  | 5000 | 1 | 2% | 5000 | 547.5 | 58.3708 | 0.0090036 | 1868.1475 | 0.030722 |  |  | Heating
| VAV |  |  | 2500 | 1 | 2% | 2500 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 |  |  | Heating
| VAV |  |  | 7000 | 1 | 2% | 7000 | 766.5 | 81.7191 | 0.012605 | 2615.4066 | 0.04301 |  |  | Heating
| VAV |  |  | 1500 | 1 | 2% | 1500 | 164.25 | 17.5112 | 0.0027011 | 560.4443 | 0.0092165 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 1500 | 1 | 2% | 1500 | 164.25 | 17.5112 | 0.0027011 | 560.4443 | 0.0092165 |  |  | Heating
| VAV |  |  | 1500 | 1 | 2% | 1500 | 164.25 | 17.5112 | 0.0027011 | 560.4443 | 0.0092165 |  |  | Heating
| VAV |  |  | 2500 | 1 | 2% | 2500 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 |  |  | Heating
| VAV |  |  | 1000 | 1 | 2% | 1000 | 109.5 | 11.6742 | 0.0018007 | 373.6295 | 0.0061443 |  |  | Heating
| VAV |  |  | 1000 | 1 | 2% | 1000 | 109.5 | 11.6742 | 0.0018007 | 373.6295 | 0.0061443 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 1000 | 1 | 2% | 1000 | 109.5 | 11.6742 | 0.0018007 | 373.6295 | 0.0061443 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 7000 | 1 | 2% | 7000 | 766.5 | 81.7191 | 0.012605 | 2615.4066 | 0.04301 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 1500 | 1 | 2% | 1500 | 164.25 | 17.5112 | 0.0027011 | 560.4443 | 0.0092165 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 1000 | 1 | 2% | 1000 | 109.5 | 11.6742 | 0.0018007 | 373.6295 | 0.0061443 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 5000 | 1 | 2% | 5000 | 547.5 | 58.3708 | 0.0090036 | 1868.1475 | 0.030722 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 0 | 1 | 2% | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 1500 | 1 | 2% | 1500 | 164.25 | 17.5112 | 0.0027011 | 560.4443 | 0.0092165 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 1500 | 1 | 2% | 1500 | 164.25 | 17.5112 | 0.0027011 | 560.4443 | 0.0092165 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 1500 | 1 | 2% | 1500 | 164.25 | 17.5112 | 0.0027011 | 560.4443 | 0.0092165 |  |  | Heating
| VAV |  |  | 1500 | 1 | 2% | 1500 | 164.25 | 17.5112 | 0.0027011 | 560.4443 | 0.0092165 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 1000 | 1 | 2% | 1000 | 109.5 | 11.6742 | 0.0018007 | 373.6295 | 0.0061443 |  |  | Heating
| VAV |  |  | 1500 | 1 | 2% | 1500 | 164.25 | 17.5112 | 0.0027011 | 560.4443 | 0.0092165 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 1500 | 1 | 2% | 1500 | 164.25 | 17.5112 | 0.0027011 | 560.4443 | 0.0092165 |  |  | Heating
| VAV |  |  | 5000 | 1 | 2% | 5000 | 547.5 | 58.3708 | 0.0090036 | 1868.1475 | 0.030722 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 6000 | 1 | 2% | 6000 | 657 | 70.045 | 0.010804 | 2241.7771 | 0.036866 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 2500 | 1 | 2% | 2500 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 |  |  | Heating
| VAV |  |  | 2500 | 1 | 2% | 2500 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 3000 | 1 | 2% | 3000 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 2000 | 1 | 2% | 2000 | 219 | 23.3483 | 0.0036014 | 747.259 | 0.012289 |  |  | Heating
| VAV |  |  | 2500 | 1 | 2% | 2500 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
| VAV |  |  | 4000 | 1 | 2% | 4000 | 438 | 46.6966 | 0.0072029 | 1494.518 | 0.024577 |  |  | Heating
313 | WH | Water Heater | 38 Amp instant hot | 4000 | 1 | 75% | 4000 | 16425 | 1751.1241 | 0.27011 | 56044.4263 | 0.92165 | VTU3-20 | 1 | DHW | Mar 12, 2018 @ 15:37 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
109 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:37 | Mar 12, 2018 @ 14:31 | mcoalson@hanson-inc.com
110 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:37 | Mar 12, 2018 @ 14:31 | mcoalson@hanson-inc.com
128 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:40 | Mar 12, 2018 @ 14:34 | mcoalson@hanson-inc.com
150 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:43 | Mar 12, 2018 @ 14:37 | mcoalson@hanson-inc.com
153 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:44 | Mar 12, 2018 @ 14:37 | mcoalson@hanson-inc.com
203 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:55 | Mar 12, 2018 @ 14:48 | mcoalson@hanson-inc.com
205 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:55 | Mar 12, 2018 @ 14:48 | mcoalson@hanson-inc.com
206 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:55 | Mar 12, 2018 @ 14:48 | mcoalson@hanson-inc.com
207 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:55 | Mar 12, 2018 @ 14:48 | mcoalson@hanson-inc.com
213 | T8 | Light Fixture | 2 2*4 2 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:56 | Mar 12, 2018 @ 14:52 | mcoalson@hanson-inc.com
16 | LF | Lighting Fixture | 2 24w CFL, 24/7 | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | M401 | 0 | Lighting | Mar 12, 2018 @ 13:55 | Mar 12, 2018 @ 13:56 | nboyd@hanson-inc.com
725 | T8 | Light Fixture | 2 4' | 24 | 2 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:47 | Mar 14, 2018 @ 13:47 | nboyd@hanson-inc.com
243 | T8 | Light Fixture | 4 4' | 12 | 4 | 100% | 48 | 262.8 | 28.018 | 0.0043217 | 896.7108 | 0.014746 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:01 | Mar 12, 2018 @ 15:01 | nboyd@hanson-inc.com
676 | LF | Lighting Fixture | 50w halogen quarts | 50 | 1 | 100% | 50 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:24 | Mar 14, 2018 @ 13:24 | nboyd@hanson-inc.com
946 | LF | Lighting Fixture | 2 25w incandescent | 25 | 2 | 100% | 50 | 273.75 | 29.1854 | 0.0045018 | 934.0738 | 0.015361 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:51 | Mar 14, 2018 @ 15:51 | nboyd@hanson-inc.com
614 | LD | LED Fixture | 60W | 60 | 1 | 100% | 60 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:24 | Mar 12, 2018 @ 19:21 | mcoalson@hanson-inc.com
1041 | LF | Lighting Fixture | 60W desk lamp | 60 | 1 | 100% | 60 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:06 | Mar 14, 2018 @ 16:06 | mcoalson@hanson-inc.com
332 | LF | Lighting Fixture | Desk lamp 60W 1b | 60 | 1 | 100% | 60 | 328.5 | 35.0225 | 0.0054022 | 1120.8885 | 0.018433 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:44 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
988 | LF | Lighting Fixture | 72w desk lamp | 72 | 1 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:58 | Mar 14, 2018 @ 15:58 | mcoalson@hanson-inc.com
1066 | T8 | Light Fixture | 2 2*2 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:24 | Mar 14, 2018 @ 16:24 | mcoalson@hanson-inc.com
990 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:58 | Mar 14, 2018 @ 15:59 | mcoalson@hanson-inc.com
999 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:04 | Mar 14, 2018 @ 16:00 | mcoalson@hanson-inc.com
1003 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:01 | Mar 14, 2018 @ 16:01 | mcoalson@hanson-inc.com
1026 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:04 | Mar 14, 2018 @ 16:04 | mcoalson@hanson-inc.com
1042 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:07 | Mar 14, 2018 @ 16:07 | mcoalson@hanson-inc.com
1078 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:26 | Mar 14, 2018 @ 16:27 | mcoalson@hanson-inc.com
639 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 12, 2018 @ 19:51 | Mar 12, 2018 @ 19:45 | mcoalson@hanson-inc.com
643 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 12, 2018 @ 19:55 | Mar 12, 2018 @ 19:49 | mcoalson@hanson-inc.com
677 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:24 | Mar 14, 2018 @ 13:24 | mcoalson@hanson-inc.com
701 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:29 | Mar 14, 2018 @ 13:32 | mcoalson@hanson-inc.com
746 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:05 | Mar 14, 2018 @ 14:06 | mcoalson@hanson-inc.com
755 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:13 | Mar 14, 2018 @ 14:14 | mcoalson@hanson-inc.com
826 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:56 | Mar 14, 2018 @ 14:50 | mcoalson@hanson-inc.com
827 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:56 | Mar 14, 2018 @ 14:50 | mcoalson@hanson-inc.com
828 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:56 | Mar 14, 2018 @ 14:50 | mcoalson@hanson-inc.com
829 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:50 | mcoalson@hanson-inc.com
832 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:51 | mcoalson@hanson-inc.com
833 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:51 | mcoalson@hanson-inc.com
834 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:51 | mcoalson@hanson-inc.com
835 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:57 | Mar 14, 2018 @ 14:51 | mcoalson@hanson-inc.com
840 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:53 | Mar 14, 2018 @ 14:53 | mcoalson@hanson-inc.com
855 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 15:02 | Mar 14, 2018 @ 14:56 | mcoalson@hanson-inc.com
865 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 15:04 | Mar 14, 2018 @ 14:58 | mcoalson@hanson-inc.com
32 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:14 | Mar 12, 2018 @ 14:08 | mcoalson@hanson-inc.com
44 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:17 | Mar 12, 2018 @ 14:11 | mcoalson@hanson-inc.com
263 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:19 | Mar 12, 2018 @ 15:13 | mcoalson@hanson-inc.com
276 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:22 | Mar 12, 2018 @ 15:16 | mcoalson@hanson-inc.com
288 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:25 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
1011 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:09 | Mar 14, 2018 @ 16:03 | mcoalson@hanson-inc.com
1040 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:12 | Mar 14, 2018 @ 16:06 | mcoalson@hanson-inc.com
315 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:39 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
318 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:40 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
321 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:42 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
326 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:43 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
337 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:46 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
338 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:47 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
353 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:51 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
360 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:53 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
363 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:54 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
365 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:55 | Mar 12, 2018 @ 18:30 | mcoalson@hanson-inc.com
384 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:39 | Mar 12, 2018 @ 18:33 | mcoalson@hanson-inc.com
393 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:42 | Mar 12, 2018 @ 18:35 | mcoalson@hanson-inc.com
395 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:42 | Mar 12, 2018 @ 18:36 | mcoalson@hanson-inc.com
466 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:06 | Mar 12, 2018 @ 19:00 | mcoalson@hanson-inc.com
471 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:07 | Mar 12, 2018 @ 19:00 | mcoalson@hanson-inc.com
479 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:09 | Mar 12, 2018 @ 19:02 | mcoalson@hanson-inc.com
493 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:10 | Mar 12, 2018 @ 19:04 | mcoalson@hanson-inc.com
503 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:11 | Mar 12, 2018 @ 19:05 | mcoalson@hanson-inc.com
515 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:12 | Mar 12, 2018 @ 19:06 | mcoalson@hanson-inc.com
525 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:14 | Mar 12, 2018 @ 19:08 | mcoalson@hanson-inc.com
541 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:15 | Mar 12, 2018 @ 19:09 | mcoalson@hanson-inc.com
555 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:17 | Mar 12, 2018 @ 19:11 | mcoalson@hanson-inc.com
568 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:19 | Mar 12, 2018 @ 19:13 | mcoalson@hanson-inc.com
583 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:21 | Mar 12, 2018 @ 19:15 | mcoalson@hanson-inc.com
598 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:22 | Mar 12, 2018 @ 19:16 | mcoalson@hanson-inc.com
606 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:23 | Mar 12, 2018 @ 19:17 | mcoalson@hanson-inc.com
620 | T8 | Light Fixture | 2 2*4 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:28 | Mar 12, 2018 @ 19:21 | mcoalson@hanson-inc.com
943 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:50 | Mar 14, 2018 @ 15:50 | nboyd@hanson-inc.com
959 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:52 | Mar 14, 2018 @ 15:53 | nboyd@hanson-inc.com
991 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:58 | Mar 14, 2018 @ 15:59 | nboyd@hanson-inc.com
1075 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:26 | Mar 14, 2018 @ 16:26 | nboyd@hanson-inc.com
646 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 12, 2018 @ 19:49 | Mar 12, 2018 @ 19:49 | nboyd@hanson-inc.com
659 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:19 | Mar 14, 2018 @ 13:19 | nboyd@hanson-inc.com
661 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:20 | Mar 14, 2018 @ 13:20 | nboyd@hanson-inc.com
697 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:28 | Mar 14, 2018 @ 13:28 | nboyd@hanson-inc.com
706 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:31 | Mar 14, 2018 @ 13:31 | nboyd@hanson-inc.com
787 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:31 | Mar 14, 2018 @ 14:32 | nboyd@hanson-inc.com
839 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:53 | Mar 14, 2018 @ 14:53 | nboyd@hanson-inc.com
18 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:03 | Mar 12, 2018 @ 14:03 | nboyd@hanson-inc.com
29 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:07 | Mar 12, 2018 @ 14:07 | nboyd@hanson-inc.com
41 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:09 | Mar 12, 2018 @ 14:10 | nboyd@hanson-inc.com
51 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:12 | Mar 12, 2018 @ 14:12 | nboyd@hanson-inc.com
61 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:18 | Mar 12, 2018 @ 14:18 | nboyd@hanson-inc.com
69 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:21 | Mar 12, 2018 @ 14:21 | nboyd@hanson-inc.com
75 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:22 | Mar 12, 2018 @ 14:22 | nboyd@hanson-inc.com
90 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:27 | Mar 12, 2018 @ 14:27 | nboyd@hanson-inc.com
97 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:28 | Mar 12, 2018 @ 14:28 | nboyd@hanson-inc.com
105 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:30 | Mar 12, 2018 @ 14:30 | nboyd@hanson-inc.com
117 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:31 | Mar 12, 2018 @ 14:31 | nboyd@hanson-inc.com
137 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:35 | Mar 12, 2018 @ 14:35 | nboyd@hanson-inc.com
147 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:36 | Mar 12, 2018 @ 14:37 | nboyd@hanson-inc.com
173 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:42 | Mar 12, 2018 @ 14:42 | nboyd@hanson-inc.com
192 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:46 | Mar 12, 2018 @ 14:46 | nboyd@hanson-inc.com
204 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:48 | Mar 12, 2018 @ 14:48 | nboyd@hanson-inc.com
218 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:50 | Mar 12, 2018 @ 14:51 | nboyd@hanson-inc.com
431 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:43 | Mar 12, 2018 @ 18:43 | nboyd@hanson-inc.com
443 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:54 | Mar 12, 2018 @ 18:55 | nboyd@hanson-inc.com
467 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:00 | Mar 12, 2018 @ 19:00 | nboyd@hanson-inc.com
476 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:02 | Mar 12, 2018 @ 19:02 | nboyd@hanson-inc.com
498 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:05 | Mar 12, 2018 @ 19:05 | nboyd@hanson-inc.com
523 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:08 | Mar 12, 2018 @ 19:08 | nboyd@hanson-inc.com
1060 | RM | Room | 113h |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:23 | Mar 14, 2018 @ 16:23 | nboyd@hanson-inc.com
1067 | RM | Room | 113c always cold |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 0 | #N/A | Mar 14, 2018 @ 16:24 | Mar 14, 2018 @ 16:28 | nboyd@hanson-inc.com
545 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:09 | Mar 12, 2018 @ 19:09 | nboyd@hanson-inc.com
564 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:13 | Mar 12, 2018 @ 19:13 | nboyd@hanson-inc.com
612 | T8 | Light Fixture | 2 2*4*3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:17 | Mar 12, 2018 @ 19:18 | nboyd@hanson-inc.com
162 | T8 | Light Fixture | 2 2*4*3, buzzing ballast | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:39 | Mar 12, 2018 @ 14:39 | nboyd@hanson-inc.com
17 | T8 | Light Fixture | 2 4' 3 | 36 | 2 | 100% | 72 | 394.2 | 42.027 | 0.0064826 | 1345.0662 | 0.02212 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:09 | Mar 12, 2018 @ 14:03 | mcoalson@hanson-inc.com
380 | T8 | Light Fixture | 7 1*2 1 | 12 | 7 | 100% | 84 | 459.9 | 49.0315 | 0.007563 | 1569.2439 | 0.025806 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:59 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
651 | T8 | Light Fixture | 4 .5*4 2 | 24 | 4 | 100% | 96 | 525.6 | 56.036 | 0.0086435 | 1793.4216 | 0.029493 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:10 | Mar 14, 2018 @ 13:06 | mcoalson@hanson-inc.com
1034 | LF | Lighting Fixture | 100W desk lamp | 100 | 1 | 100% | 100 | 547.5 | 58.3708 | 0.0090036 | 1868.1475 | 0.030722 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:06 | Mar 14, 2018 @ 16:06 | mcoalson@hanson-inc.com
171 | LF | Lighting Fixture | Desk lamp 1 100W | 100 | 1 | 100% | 100 | 547.5 | 58.3708 | 0.0090036 | 1868.1475 | 0.030722 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:48 | Mar 12, 2018 @ 14:41 | mcoalson@hanson-inc.com
699 | T8 | Light Fixture | 3 2*4 3 | 36 | 3 | 100% | 108 | 591.3 | 63.0405 | 0.0097239 | 2017.5993 | 0.033179 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:35 | Mar 14, 2018 @ 13:29 | mcoalson@hanson-inc.com
727 | T8 | Light Fixture | 3 2*4 3 | 36 | 3 | 100% | 108 | 591.3 | 63.0405 | 0.0097239 | 2017.5993 | 0.033179 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:48 | Mar 14, 2018 @ 13:49 | mcoalson@hanson-inc.com
1054 | MS | Miscellaneous | 2 dry goods vending machines. | 250 | 2 | 75% | 500 | 2053.125 | 218.8905 | 0.033764 | 7005.5533 | 0.11521 | 1st Floor | 3 | Plug Load | Mar 14, 2018 @ 16:20 | Mar 14, 2018 @ 16:21 | mcoalson@hanson-inc.com
1001 | M | Monitor | 2 Coun | 21 | 2 | 100% | 42 | 229.95 | 24.5157 | 0.0037815 | 784.622 | 0.012903 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:07 | Mar 14, 2018 @ 16:00 | mcoalson@hanson-inc.com
1015 | M | Monitor | 2 Count | 21 | 2 | 100% | 42 | 229.95 | 24.5157 | 0.0037815 | 784.622 | 0.012903 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:10 | Mar 14, 2018 @ 16:03 | mcoalson@hanson-inc.com
1035 | M | Monitor | 2 Count | 21 | 2 | 100% | 42 | 229.95 | 24.5157 | 0.0037815 | 784.622 | 0.012903 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:12 | Mar 14, 2018 @ 16:06 | mcoalson@hanson-inc.com
973 | TV | Television | 2 Count | 175 | 2 | 25% | 350 | 479.0625 | 51.0745 | 0.0078782 | 1634.6291 | 0.026881 | 1st Floor | 2 | Plug Load | Mar 14, 2018 @ 16:01 | Mar 14, 2018 @ 16:00 | mcoalson@hanson-inc.com
1052 | MS | Miscellaneous | 3 Soda machines. See pics | 1000 | 3 | 75% | 3000 | 12318.75 | 1313.3431 | 0.20258 | 42033.3197 | 0.69124 | 1st Floor | 4 | Plug Load | Mar 14, 2018 @ 16:18 | Mar 14, 2018 @ 16:20 | mcoalson@hanson-inc.com
57 | T8 | Light Fixture | 3 2*4 3 | 36 | 3 | 100% | 108 | 591.3 | 63.0405 | 0.0097239 | 2017.5993 | 0.033179 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:19 | Mar 12, 2018 @ 14:13 | mcoalson@hanson-inc.com
289 | T8 | Light Fixture | 3 2*4 3 | 36 | 3 | 100% | 108 | 591.3 | 63.0405 | 0.0097239 | 2017.5993 | 0.033179 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:26 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
926 | VF | VFD |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 1st Floor | 2 | #N/A | Mar 14, 2018 @ 15:32 | Mar 14, 2018 @ 15:32 | nboyd@hanson-inc.com
652 | VF | VFD |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 2nd Floor | 1 | #N/A | Mar 14, 2018 @ 13:09 | Mar 14, 2018 @ 13:10 | nboyd@hanson-inc.com
12 | VF | VFD | AHU-3 VFD |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | M401 | 2 | #N/A | Mar 12, 2018 @ 13:47 | Mar 12, 2018 @ 13:47 | nboyd@hanson-inc.com
300 | T8 | Light Fixture | 3 2*4 3 | 36 | 3 | 100% | 108 | 591.3 | 63.0405 | 0.0097239 | 2017.5993 | 0.033179 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:31 | Mar 12, 2018 @ 18:28 | mcoalson@hanson-inc.com
965 | T8 | Light Fixture | 3 2*4 3 | 36 | 3 | 100% | 108 | 591.3 | 63.0405 | 0.0097239 | 2017.5993 | 0.033179 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:53 | Mar 14, 2018 @ 15:53 | mcoalson@hanson-inc.com
452 | T8 | Light Fixture | 3 2*4 3 | 36 | 3 | 100% | 108 | 591.3 | 63.0405 | 0.0097239 | 2017.5993 | 0.033179 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:02 | Mar 12, 2018 @ 18:56 | mcoalson@hanson-inc.com
691 | T8 | Light Fixture | 3 2*4*3 | 36 | 3 | 100% | 108 | 591.3 | 63.0405 | 0.0097239 | 2017.5993 | 0.033179 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:27 | Mar 14, 2018 @ 13:27 | nboyd@hanson-inc.com
260 | T8 | Light Fixture | 3 2*4*3 | 36 | 3 | 100% | 108 | 591.3 | 63.0405 | 0.0097239 | 2017.5993 | 0.033179 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:10 | Mar 12, 2018 @ 15:11 | nboyd@hanson-inc.com
266 | T8 | Light Fixture | 3 2*4*3 | 36 | 3 | 100% | 108 | 591.3 | 63.0405 | 0.0097239 | 2017.5993 | 0.033179 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:13 | Mar 12, 2018 @ 15:13 | nboyd@hanson-inc.com
887 | T8 | Light Fixture | 3 2*4*3 24/7 | 36 | 3 | 160% | 108 | 946.08 | 100.8647 | 0.015558 | 3228.159 | 0.053087 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:09 | Mar 14, 2018 @ 15:10 | nboyd@hanson-inc.com
125 | LF | Lighting Fixture | Desk lamp 2 60W | 60 | 2 | 100% | 120 | 657 | 70.045 | 0.010804 | 2241.7771 | 0.036866 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:39 | Mar 12, 2018 @ 14:33 | mcoalson@hanson-inc.com
200 | LF | Lighting Fixture | Desk lamp 2 60W | 60 | 2 | 100% | 120 | 657 | 70.045 | 0.010804 | 2241.7771 | 0.036866 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:54 | Mar 12, 2018 @ 14:47 | mcoalson@hanson-inc.com
225 | T8 | Light Fixture | 2 2*4 5 | 60 | 2 | 100% | 120 | 657 | 70.045 | 0.010804 | 2241.7771 | 0.036866 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:58 | Mar 12, 2018 @ 14:52 | mcoalson@hanson-inc.com
930 | T8 | Light Fixture | 5 .5*4 2 | 24 | 5 | 100% | 120 | 657 | 70.045 | 0.010804 | 2241.7771 | 0.036866 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:44 | Mar 14, 2018 @ 15:38 | mcoalson@hanson-inc.com
961 | T8 | Light Fixture | 4 2*4 3 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:53 | Mar 14, 2018 @ 15:53 | mcoalson@hanson-inc.com
974 | T8 | Light Fixture | 4 2*4 3 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:55 | Mar 14, 2018 @ 15:55 | mcoalson@hanson-inc.com
656 | T8 | Light Fixture | 4 2*4 3 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:25 | Mar 14, 2018 @ 13:20 | mcoalson@hanson-inc.com
673 | T8 | Light Fixture | 4 2*4 3 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:30 | Mar 14, 2018 @ 13:25 | mcoalson@hanson-inc.com
686 | T8 | Light Fixture | 4 2*4 3 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:32 | Mar 14, 2018 @ 13:27 | mcoalson@hanson-inc.com
245 | T8 | Light Fixture | 4 2*4 3 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:09 | Mar 12, 2018 @ 15:03 | mcoalson@hanson-inc.com
370 | T8 | Light Fixture | 4 2*4 3 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:56 | Mar 12, 2018 @ 18:31 | mcoalson@hanson-inc.com
912 | T8 | Light Fixture | 4 2*4*3 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:19 | Mar 14, 2018 @ 15:19 | nboyd@hanson-inc.com
1007 | T8 | Light Fixture | 4 2*4*3 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:02 | Mar 14, 2018 @ 16:02 | nboyd@hanson-inc.com
397 | T8 | Light Fixture | 4 2*4*3 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:36 | Mar 12, 2018 @ 18:36 | nboyd@hanson-inc.com
434 | T8 | Light Fixture | 4 2*4*3 24/7 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:45 | Mar 12, 2018 @ 18:47 | nboyd@hanson-inc.com
877 | T8 | Light Fixture | 4 2*4*3, 2 run 24/7 | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:59 | Mar 14, 2018 @ 15:02 | nboyd@hanson-inc.com
824 | LF | Lighting Fixture | 4 4p 2b | 36 | 4 | 100% | 144 | 788.4 | 84.054 | 0.012965 | 2690.1325 | 0.044239 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:55 | Mar 14, 2018 @ 14:49 | mcoalson@hanson-inc.com
719 | LF | Lighting Fixture | 150w hps | 150 | 1 | 100% | 150 | 821.25 | 87.5562 | 0.013505 | 2802.2213 | 0.046082 | 2nd Floor | 1 | Lighting | Mar 14, 2018 @ 13:43 | Mar 14, 2018 @ 13:43 | nboyd@hanson-inc.com
25 | LF | Lighting Fixture | Office lamp 2 75W bulb | 75 | 2 | 100% | 150 | 821.25 | 87.5562 | 0.013505 | 2802.2213 | 0.046082 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 14:12 | Mar 12, 2018 @ 14:06 | mcoalson@hanson-inc.com
851 | T8 | Light Fixture | 13 W | 13 | 13 | 100% | 169 | 925.275 | 98.6467 | 0.015216 | 3157.1693 | 0.051919 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:55 | Mar 14, 2018 @ 14:56 | mcoalson@hanson-inc.com
867 | LF | Lighting Fixture | 13w cfl | 13 | 13 | 100% | 169 | 925.275 | 98.6467 | 0.015216 | 3157.1693 | 0.051919 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:58 | Mar 14, 2018 @ 14:58 | nboyd@hanson-inc.com
1053 | T8 | Light Fixture | 5 2*2 3 | 36 | 5 | 100% | 180 | 985.5 | 105.0674 | 0.016206 | 3362.6656 | 0.055299 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:25 | Mar 14, 2018 @ 16:22 | mcoalson@hanson-inc.com
310 | T8 | Light Fixture | 5 2*4 3 | 36 | 5 | 100% | 180 | 985.5 | 105.0674 | 0.016206 | 3362.6656 | 0.055299 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:34 | Mar 12, 2018 @ 18:29 | mcoalson@hanson-inc.com
446 | T8 | Light Fixture | 5 2*4 3 | 36 | 5 | 100% | 180 | 985.5 | 105.0674 | 0.016206 | 3362.6656 | 0.055299 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:02 | Mar 12, 2018 @ 18:55 | mcoalson@hanson-inc.com
960 | DT | Desktop | 6 Count | 50 | 6 | 90% | 300 | 1478.25 | 157.6012 | 0.02431 | 5043.9984 | 0.082948 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:59 | Mar 14, 2018 @ 16:00 | mcoalson@hanson-inc.com
441 | T8 | Light Fixture | 5 2*4 3 | 36 | 5 | 100% | 180 | 985.5 | 105.0674 | 0.016206 | 3362.6656 | 0.055299 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:00 | Mar 12, 2018 @ 18:54 | mcoalson@hanson-inc.com
741 | LF | Lighting Fixture | 2 100w incandescent track lighting | 100 | 2 | 100% | 200 | 1095 | 116.7416 | 0.018007 | 3736.2951 | 0.061443 | 2nd Floor | 1 | Lighting | Mar 14, 2018 @ 13:59 | Mar 14, 2018 @ 14:01 | nboyd@hanson-inc.com
435 | T8 | Light Fixture | 6 2*2*3 24/7 | 36 | 6 | 100% | 216 | 1182.6 | 126.0809 | 0.019448 | 4035.1987 | 0.066359 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:46 | Mar 12, 2018 @ 18:47 | nboyd@hanson-inc.com
907 | T8 | Light Fixture | 6 2*4 3 | 36 | 6 | 100% | 216 | 1182.6 | 126.0809 | 0.019448 | 4035.1987 | 0.066359 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:19 | Mar 14, 2018 @ 15:17 | mcoalson@hanson-inc.com
425 | T8 | Light Fixture | 6 2*4 3 | 36 | 6 | 100% | 216 | 1182.6 | 126.0809 | 0.019448 | 4035.1987 | 0.066359 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:48 | Mar 12, 2018 @ 18:42 | mcoalson@hanson-inc.com
853 | T8 | Light Fixture | 6 2*4*3 | 36 | 6 | 100% | 216 | 1182.6 | 126.0809 | 0.019448 | 4035.1987 | 0.066359 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:56 | Mar 14, 2018 @ 14:56 | nboyd@hanson-inc.com
246 | T8 | Light Fixture | 7 2*2*3 | 36 | 7 | 100% | 252 | 1379.7 | 147.0944 | 0.022689 | 4707.7318 | 0.077418 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:03 | Mar 12, 2018 @ 15:03 | nboyd@hanson-inc.com
941 | T8 | Light Fixture | 7 2*4 3 | 36 | 7 | 100% | 252 | 1379.7 | 147.0944 | 0.022689 | 4707.7318 | 0.077418 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:48 | Mar 14, 2018 @ 15:50 | mcoalson@hanson-inc.com
1055 | LF | Lighting Fixture | 7 4p 2b | 36 | 7 | 100% | 252 | 1379.7 | 147.0944 | 0.022689 | 4707.7318 | 0.077418 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:26 | Mar 14, 2018 @ 16:20 | mcoalson@hanson-inc.com
796 | LF | Lighting Fixture | 7 4p 2b recessed | 36 | 7 | 100% | 252 | 1379.7 | 147.0944 | 0.022689 | 4707.7318 | 0.077418 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:39 | Mar 14, 2018 @ 14:40 | mcoalson@hanson-inc.com
626 | LF | Lighting Fixture | 7 4p 2b recessed | 36 | 7 | 100% | 252 | 1379.7 | 147.0944 | 0.022689 | 4707.7318 | 0.077418 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:34 | Mar 12, 2018 @ 19:28 | mcoalson@hanson-inc.com
631 | T8 | Light Fixture | 7 2*4*3 24/7 | 36 | 7 | 160% | 252 | 2207.52 | 235.3511 | 0.036303 | 7532.3709 | 0.12387 | 2nd Floor | 0 | Lighting | Mar 12, 2018 @ 19:38 | Mar 12, 2018 @ 19:39 | nboyd@hanson-inc.com
753 | T8 | Light Fixture | 8 2*2 3 | 36 | 8 | 100% | 288 | 1576.8 | 168.1079 | 0.02593 | 5380.2649 | 0.088478 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:19 | Mar 14, 2018 @ 14:13 | mcoalson@hanson-inc.com
627 | T8 | Light Fixture | 9 2*4 3 | 36 | 9 | 100% | 324 | 1773.9 | 189.1214 | 0.029172 | 6052.798 | 0.099538 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 19:35 | Mar 12, 2018 @ 19:29 | mcoalson@hanson-inc.com
15 | LF | Lighting Fixture | 7 50w halogen a19 , 24/7 | 50 | 7 | 100% | 350 | 1916.25 | 204.2978 | 0.031513 | 6538.5164 | 0.10753 | M401 | 0 | Lighting | Mar 12, 2018 @ 13:54 | Mar 12, 2018 @ 13:57 | nboyd@hanson-inc.com
723 | T8 | Light Fixture | 10 2*4 3 | 36 | 10 | 100% | 360 | 1971 | 210.1349 | 0.032413 | 6725.3312 | 0.1106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:47 | Mar 14, 2018 @ 13:47 | mcoalson@hanson-inc.com
635 | MS | Miscellaneous | 8 TV | 175 | 8 | 25% | 1400 | 1916.25 | 204.2978 | 0.031513 | 6538.5164 | 0.10753 | 2nd Floor | 2 | Plug Load | Mar 12, 2018 @ 19:47 | Mar 12, 2018 @ 19:42 | mcoalson@hanson-inc.com
648 | TV | Television | 8 Touch screen computer TV | 175 | 8 | 25% | 1400 | 1916.25 | 204.2978 | 0.031513 | 6538.5164 | 0.10753 | 2nd Floor | 3 | Plug Load | Mar 14, 2018 @ 12:56 | Mar 14, 2018 @ 12:58 | mcoalson@hanson-inc.com
763 | LF | Lighting Fixture | 10 4p 2b | 36 | 10 | 100% | 360 | 1971 | 210.1349 | 0.032413 | 6725.3312 | 0.1106 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:21 | Mar 14, 2018 @ 14:15 | mcoalson@hanson-inc.com
944 | LF | Lighting Fixture | 11 4p 2b | 36 | 11 | 100% | 396 | 2168.1 | 231.1484 | 0.035654 | 7397.8643 | 0.12166 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:57 | Mar 14, 2018 @ 15:51 | mcoalson@hanson-inc.com
1046 | LF | Lighting Fixture | 11 4p 2b | 36 | 11 | 100% | 396 | 2168.1 | 231.1484 | 0.035654 | 7397.8643 | 0.12166 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:20 | Mar 14, 2018 @ 16:13 | mcoalson@hanson-inc.com
729 | LF | Lighting Fixture | 11 4p 2b | 36 | 11 | 100% | 396 | 2168.1 | 231.1484 | 0.035654 | 7397.8643 | 0.12166 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:55 | Mar 14, 2018 @ 13:49 | mcoalson@hanson-inc.com
734 | LF | Lighting Fixture | 11 4p 2b recessed | 36 | 11 | 100% | 396 | 2168.1 | 231.1484 | 0.035654 | 7397.8643 | 0.12166 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:55 | Mar 14, 2018 @ 13:56 | mcoalson@hanson-inc.com
792 | LF | Lighting Fixture | 11 4p 2b recessed | 36 | 11 | 100% | 396 | 2168.1 | 231.1484 | 0.035654 | 7397.8643 | 0.12166 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:32 | Mar 14, 2018 @ 14:32 | mcoalson@hanson-inc.com
1045 | LF | Lighting Fixture | 11 4p 2b recessed 32W | 36 | 11 | 100% | 396 | 2168.1 | 231.1484 | 0.035654 | 7397.8643 | 0.12166 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 16:13 | Mar 14, 2018 @ 16:14 | mcoalson@hanson-inc.com
722 | LF | Lighting Fixture | 11 4p 2b recessed can | 36 | 11 | 100% | 396 | 2168.1 | 231.1484 | 0.035654 | 7397.8643 | 0.12166 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:46 | Mar 14, 2018 @ 13:47 | nboyd@hanson-inc.com
976 | LF | Lighting Fixture | 12 4p 2b recessed 32W | 36 | 12 | 100% | 432 | 2365.2 | 252.1619 | 0.038896 | 8070.3974 | 0.13272 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:55 | Mar 14, 2018 @ 15:55 | mcoalson@hanson-inc.com
636 | LF | Lighting Fixture | 20 2*2 led | 24 | 20 | 100% | 480 | 2628 | 280.1799 | 0.043217 | 8967.1082 | 0.14746 | 2nd Floor | 1 | Lighting | Mar 12, 2018 @ 19:42 | Mar 12, 2018 @ 19:43 | nboyd@hanson-inc.com
433 | LF | Lighting Fixture | 8 4p 2b 32W | 64 | 8 | 100% | 512 | 2803.2 | 298.8585 | 0.046098 | 9564.9154 | 0.15729 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:50 | Mar 12, 2018 @ 18:45 | mcoalson@hanson-inc.com
891 | T8 | Light Fixture | 15 2*4*3, 1 24/7 | 36 | 15 | 100% | 540 | 2956.5 | 315.2023 | 0.048619 | 10087.9967 | 0.1659 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:11 | Mar 14, 2018 @ 15:11 | nboyd@hanson-inc.com
934 | T8 | Light Fixture | 16 2*2 3 | 36 | 16 | 100% | 576 | 3153.6 | 336.2158 | 0.051861 | 10760.5299 | 0.17696 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:53 | Mar 14, 2018 @ 15:47 | mcoalson@hanson-inc.com
940 | T8 | Light Fixture | 16 2*4 3 | 36 | 16 | 100% | 576 | 3153.6 | 336.2158 | 0.051861 | 10760.5299 | 0.17696 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:54 | Mar 14, 2018 @ 15:49 | mcoalson@hanson-inc.com
717 | LF | Lighting Fixture | 16 4P 2b recessed | 36 | 16 | 100% | 576 | 3153.6 | 336.2158 | 0.051861 | 10760.5299 | 0.17696 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:47 | Mar 14, 2018 @ 13:42 | mcoalson@hanson-inc.com
825 | LF | Lighting Fixture | 4 150w hps | 150 | 4 | 100% | 600 | 3285 | 350.2248 | 0.054022 | 11208.8853 | 0.18433 | 2nd Floor | 1 | Lighting | Mar 14, 2018 @ 14:49 | Mar 14, 2018 @ 14:50 | nboyd@hanson-inc.com
888 | LF | Lighting Fixture | 17 4p 2b recessed | 36 | 17 | 100% | 612 | 3350.7 | 357.2293 | 0.055102 | 11433.063 | 0.18802 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:10 | Mar 14, 2018 @ 15:10 | mcoalson@hanson-inc.com
247 | LF | Lighting Fixture | 10 4pin 2bulb 32w per bulb recessed can | 64 | 10 | 100% | 640 | 3504 | 373.5731 | 0.057623 | 11956.1443 | 0.19662 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:05 | Mar 12, 2018 @ 15:06 | nboyd@hanson-inc.com
253 | LF | Lighting Fixture | 11 4p 2b 32W recessed can | 64 | 11 | 100% | 704 | 3854.4 | 410.9305 | 0.063385 | 13151.7587 | 0.21628 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:13 | Mar 12, 2018 @ 15:10 | mcoalson@hanson-inc.com
255 | LF | Lighting Fixture | 11 4p 2b 32W recessed can | 64 | 11 | 100% | 704 | 3854.4 | 410.9305 | 0.063385 | 13151.7587 | 0.21628 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:13 | Mar 12, 2018 @ 15:11 | mcoalson@hanson-inc.com
240 | T8 | Light Fixture | 22 2*4 3 | 36 | 22 | 100% | 792 | 4336.2 | 462.2968 | 0.071309 | 14795.7285 | 0.24331 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:04 | Mar 12, 2018 @ 14:59 | mcoalson@hanson-inc.com
890 | T8 | Light Fixture | 25 2*4 3 | 36 | 25 | 100% | 900 | 4927.5 | 525.3372 | 0.081032 | 16813.3279 | 0.27649 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:11 | Mar 14, 2018 @ 15:11 | mcoalson@hanson-inc.com
429 | T8 | Light Fixture | 28 2*4 3 | 36 | 28 | 100% | 1008 | 5518.8 | 588.3777 | 0.090756 | 18830.9272 | 0.30967 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 18:49 | Mar 12, 2018 @ 18:44 | mcoalson@hanson-inc.com
252 | LF | Lighting Fixture | 16 4pin 2bulb 32W per bulb recessed can | 64 | 16 | 100% | 1024 | 5606.4 | 597.717 | 0.092197 | 19129.8309 | 0.31459 | VTU3-20 | 0 | Lighting | Mar 12, 2018 @ 15:13 | Mar 12, 2018 @ 15:09 | mcoalson@hanson-inc.com
920 | T8 | Light Fixture | 32 2*4 3 | 36 | 32 | 100% | 1152 | 6307.2 | 672.4317 | 0.10372 | 21521.0597 | 0.35391 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:24 | Mar 14, 2018 @ 15:24 | mcoalson@hanson-inc.com
630 | LF | Lighting Fixture | 8 wall sconce, assume 150w hps | 150 | 8 | 100% | 1200 | 6570 | 700.4496 | 0.10804 | 22417.7705 | 0.36866 | 2nd Floor | 1 | Lighting | Mar 12, 2018 @ 19:37 | Mar 14, 2018 @ 13:41 | nboyd@hanson-inc.com
726 | LF | Lighting Fixture | 34 4p 2b | 36 | 34 | 100% | 1224 | 6701.4 | 714.4586 | 0.1102 | 22866.1259 | 0.37603 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 13:54 | Mar 14, 2018 @ 13:48 | mcoalson@hanson-inc.com
892 | LF | Lighting Fixture | 40 4p 2b | 36 | 40 | 100% | 1440 | 7884 | 840.5396 | 0.12965 | 26901.3246 | 0.44239 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:16 | Mar 14, 2018 @ 15:17 | mcoalson@hanson-inc.com
915 | LF | Lighting Fixture | 48 4p 2b | 36 | 48 | 100% | 1728 | 9460.8 | 1008.6475 | 0.15558 | 32281.5896 | 0.53087 | 1st Floor | 0 | Lighting | Mar 14, 2018 @ 15:26 | Mar 14, 2018 @ 15:23 | mcoalson@hanson-inc.com
831 | T8 | Light Fixture | 8 4' per floor | 288 | 8 | 100% | 2304 | 12614.4 | 1344.8633 | 0.20744 | 43042.1194 | 0.70782 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:50 | Mar 14, 2018 @ 14:51 | nboyd@hanson-inc.com
737 | T8 | Light Fixture | 15 2*4 2 dimmable (T12) | 180 | 15 | 100% | 2700 | 14782.5 | 1576.0117 | 0.2431 | 50439.9837 | 0.82948 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:03 | Mar 14, 2018 @ 14:34 | mcoalson@hanson-inc.com
823 | 12 | T-12 Light Fixture | 15 2*4 3 | 270 | 15 | 100% | 4050 | 22173.75 | 2364.0176 | 0.36465 | 75659.9755 | 1.2442 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:54 | Mar 14, 2018 @ 14:48 | mcoalson@hanson-inc.com
803 | 12 | T-12 Light Fixture | 24 2*4 3 | 270 | 24 | 100% | 6480 | 35478 | 3782.4281 | 0.58343 | 121055.9609 | 1.9908 | 2nd Floor | 0 | Lighting | Mar 14, 2018 @ 14:47 | Mar 14, 2018 @ 14:43 | mcoalson@hanson-inc.com
881 | DT | Desktop | 71 student workstations | 50 | 71 | 90% | 3550 | 17492.625 | 1864.9472 | 0.28767 | 59687.314 | 0.98155 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:06 | Mar 14, 2018 @ 15:07 | mcoalson@hanson-inc.com
910 | DT | Desktop | 196 Count | 50 | 196 | 90% | 9800 | 48289.5 | 5148.3049 | 0.79412 | 164770.6134 | 2.7096 | 1st Floor | 2 | Plug Load | Mar 14, 2018 @ 15:24 | Mar 14, 2018 @ 15:19 | mcoalson@hanson-inc.com
908 | M | Monitor | 196 Monitors | 21 | 196 | 100% | 4116 | 22535.1 | 2402.5423 | 0.37059 | 76892.9529 | 1.2645 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:22 | Mar 14, 2018 @ 15:17 | mcoalson@hanson-inc.com
952 | M | Monitor | 12 Count | 21 | 12 | 100% | 252 | 1379.7 | 147.0944 | 0.022689 | 4707.7318 | 0.077418 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:58 | Mar 14, 2018 @ 15:52 | mcoalson@hanson-inc.com
962 | M | Monitor | 3 | 21 | 3 | 100% | 63 | 344.925 | 36.7736 | 0.0056723 | 1176.933 | 0.019355 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:53 | Mar 14, 2018 @ 15:53 | nboyd@hanson-inc.com
978 | M | Monitor | 3 | 21 | 3 | 100% | 63 | 344.925 | 36.7736 | 0.0056723 | 1176.933 | 0.019355 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:56 | Mar 14, 2018 @ 15:56 | nboyd@hanson-inc.com
992 | M | Monitor | 3 | 21 | 3 | 100% | 63 | 344.925 | 36.7736 | 0.0056723 | 1176.933 | 0.019355 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:58 | Mar 14, 2018 @ 15:59 | nboyd@hanson-inc.com
1016 | M | Monitor | 3 | 21 | 3 | 100% | 63 | 344.925 | 36.7736 | 0.0056723 | 1176.933 | 0.019355 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 16:03 | Mar 14, 2018 @ 16:03 | nboyd@hanson-inc.com
882 | M | Monitor | 71 monitors | 21 | 71 | 75% | 1491 | 6122.4187 | 652.7315 | 0.10068 | 20890.5599 | 0.34354 | 1st Floor | 0 | Plug Load | Mar 14, 2018 @ 15:07 | Mar 14, 2018 @ 15:07 | mcoalson@hanson-inc.com
[5 empty] | 2359 |  | 591171 | 1024842.8025 | 109261.9143 | 5.0431 | 3496908.7938 | 57.5064
Quick Calcs:
HP →Watts
[5 empty] | Enter HP | 30
[5 empty] | Watts | 22371
250 fixtures
|  |  | lighting avg |  | Watts → kBtu/hr→Tons
|  |  | 40 | w | Enter Watts | 388267.45
[5 empty] | kBtu/hr | 0.0068243
[5 empty] | Tons (cooling) | 0.16667
Parasitic Loss
[5 empty] | Sum Demand KVA | 1074.7
[5 empty] | kWh | 5883982.5
[5 empty] | ±5% of Elec Utility? | Use kWh
[5 empty] | Impedence Avg | 4.5%
[5 empty] | kWh Lost | 48406.5
[5 empty] | $ Value Lost | 5160.7786
[6 empty] | Length | 145
[6 empty] | Width | 144
20880

## FIM Calculations
| The numbers in this spreadsheet are all from Building 27 | [7 empty] | Suggested FIM? | Q: for Wade
| Please indicate which calculations you've completed. | [8 empty] | Heating FIMs???
1.1 | BAS Upgrade Estimates | [6 empty] | % of Total
| Labor/hr | 175 | [5 empty] | 0%
| Item | Materials | Hrs | Total | Item Count |  | Electric Annual Cost
| VAV | 178000 | 16 | 427200 | 89 |  | 114347.76 | 100%
| FCU | 0 | 0 | 0 | 0 |  | Annual Utility Costs
| DX Split | 0 | 0 | 0 | 0 |  | 114347.76
| AHU |  |  | 0 | 6
| ECM Pump | 0 | 0 | 0 | 0
| Total Cost |  |  | 427200
1.2 | Optimal Start & Schedule Alignment | [7 empty] | Yes
| New Schedule operates |  | 35% | of original | New Annual Cost |  |  |  | Yes
| Updated Cost CEP 1 & 2 |  | 0 |  | 0 |  |  |  | Yes
Yes
| Below Calculation based off changing the schedule hours of Mech Equipment | [7 empty] | Yes
| Updated Annual kWh |  | 16508.081 |  | 25412.9021 |  |  |  | Yes
Yes
| Total Savings |  |  | 25412.9021 |  |  |  |  | Yes
1.3 | Reduced min flow settings VAV terminals (25% of half the terminals) | [7 empty] | Possible with Plenum Return?
| Original W | 122500 | Chilled Water Savings Determined with Calc on CEP Utility Form | [5 empty] | Possible with Plenum Return?
| New W | 107187.5 |  | Annual Space Heater Savings |  |  |  |  | Possible with Plenum Return?
| Affinity Law | 1.4927 |  | 100 |  |  |  |  | Possible with Plenum Return?
| % Change | .492 |  | CFM Reduction |  |  |  |  | Possible with Plenum Return?
| Annual $ kWh |  |  | 584.375 |  |  |  |  | Possible with Plenum Return?
| 3168.3485 |  | 1300 | Annual kBtu Savings |  |  |  |  | Possible with Plenum Return?
|  |  |  | 12641.1317 |  |  |  |  | Possible with Plenum Return?
| Annual VAV Savings |  |  | Total Savings for FIM |  |  |  |  | Possible with Plenum Return?
| 1609.5211 |  |  | 3009.5211 |  |  |  |  | Possible with Plenum Return?
1.4 | Relax zone cooling setpoint | [7 empty] | Yes
| 15% | Expected savings 2F relaxed setpoint. | [6 empty] | Yes
| Initial Cost |  |  | 0 |  |  |  |  | Yes
| W/ savings FIM 1.1 - 1.3 implemented |  |  | 0 |  |  |  |  | Yes
| Total Savings of FIM 1.1 - 1.4 |  |  | 0 |  |  |  |  | Yes
| Savings of FIM 1.4 |  |  | 0 |  |  |  |  | Yes
| Est Annual Utility Cost for FIM 1.1-1.4 |  |  | 85925.3368 |  |  |  |  | Yes
1.5 | Eliminate OA ventilation during warm-up/cool-down | [7 empty] | Yes, but COVID
| 5% | Expected Percent Savings | [6 empty] | Yes, but COVID
| Savings for reduced CHW load |  |  | 0 |  |  |  |  | Yes, but COVID
| 3168 | Anticipated Cost of Electric reheat coil | [6 empty] | Yes, but COVID
| Savings for reduced reheat load |  |  | 158.4 |  |  |  |  | Yes, but COVID
| Total Savings for FIM 1.5 |  |  | 158.4 |  |  |  |  | Yes, but COVID
| Est Annual Utility Cost for FIM 1.1 - 1.5: |  |  | 85766.9368 |  |  |  |  | Yes, but COVID
1.6 | Implement OA econimizer mode | [7 empty] | Yes, ask Wade to double check my assesment of rtu1_ssFan. ON/OFF operation is all I can see used. Also, supposed VFD ready in notes of M6.2. Supposed to be here per 2007 reno drawings M6.2
| 5% | Expected Percent Savings | [6 empty] | Yes, ask Wade if he has an idea of how to verify with exisiting data?
| Savings for reduced CHW load |  |  | 0 |  |  |  |  | Yes, ask Wade if he has an idea of how to verify with exisiting data?
| 3009.6 | Anticipated Cost of Electric reheat coil | [6 empty] | Yes, ask Wade if he has an idea of how to verify with exisiting data?
| Savings for reduced reheat load |  |  | 150.48 |  |  |  |  | Yes, ask Wade if he has an idea of how to verify with exisiting data?
| Total Savings for FIM 1.5 |  |  | 150.48 |  |  |  |  | Yes, ask Wade if he has an idea of how to verify with exisiting data?
| Est Annual Utility Cost for FIM 1.1 - 1.6: |  |  | 85616.4568 |  |  |  |  | Yes, ask Wade if he has an idea of how to verify with exisiting data?
1.7 | Implement dynamic supply air static pressure setpoint | [7 empty] | Yes, ask Wade if he has an idea of how to verify with exisiting data?
| Est. Annual Cost of Fan Power Original |  |  | 5525 |  |  |  |  | Yes, ask Wade if he has an idea of how to verify with exisiting data?
| % of Total Electical Bill |  |  | 4.832% |  |  |  |  | Yes, ask Wade if he has an idea of how to verify with exisiting data?
| Annual savings w/10% Fan Power Reduc |  |  | 413.6775 |  |  |  |  | Yes, ask Wade if he has an idea of how to verify with exisiting data?
| Est Annual Utility Cost for FIM 1.1 - 1.7: |  |  | 85202.7794 |  |  |  |  | Yes, ask Wade if he has an idea of how to verify with exisiting data?
1.8 | Tune PID control loop routines to match VFD
| 3% | Expected % Savings
| Savings for reduced fan load |  |  | 165.75
| Est Annual Utility Cost for FIM 1.1 - 1.8: |  |  | 85037.0294
Summed Savings and Payback for FIM's 1.1-1.8
| Total Cost | 427200
| Est. Savings | 29310.7306
| Payback (yr) | 14.5749
1.9 | Implement Demand Control Ventilation | [7 empty] | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| Cost | 8000 | [6 empty] | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| 5% | Expected CHW load savings | [6 empty] | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| 3% | Expected electric reheat savings | [6 empty] | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| CHW savings |  |  | 0 |  |  |  |  | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| Electric Reheat Savings |  |  | 123.2633 |  |  |  |  | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| Total Savings for DCV |  |  | 123.2633 |  |  |  |  | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| Expected payback (yr) |  |  | 65 |  |  |  |  | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| Est Annual Utility Cost for FIM 1.1 - 1.9: |  |  | 84913.766 |  |  |  |  | Yes, it is in existing SOO, but can find no evidence of it being utilized.
1.1 | Implement Supply Air Temperature setpoint reset | [7 empty] | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| Cost | 2500 | [6 empty] | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| 3% | Expected CHW load savings | [6 empty] | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| CHW savings |  |  | 0 |  |  |  |  | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| Expected payback (yr) |  |  | #DIV/0! |  |  |  |  | Yes, it is in existing SOO, but can find no evidence of it being utilized.
| Est Annual Utility Cost for FIM 1.1 - 1.10: |  |  | 84913.766 |  |  |  |  | Yes, it is in existing SOO, but can find no evidence of it being utilized.
1.11 | Install Occupancy sensors and integrate with BAS | [7 empty] | This is a cost of 1.9 & 1.10
| Cost | 6500 | [6 empty] | This is a cost of 1.9 & 1.10
| 5% | Expected CHW load savings | [6 empty] | This is a cost of 1.9 & 1.10
| 5% | Expected electric reheat savings | [6 empty] | This is a cost of 1.9 & 1.10
| CHW savings |  |  | 0 |  |  |  |  | This is a cost of 1.9 & 1.10
| Electric Reheat Savings |  |  | 205.1411 |  |  |  |  | This is a cost of 1.9 & 1.10
| Total Savings for DCV |  |  | 205.1411 |  |  |  |  | This is a cost of 1.9 & 1.10
| Expected payback (yr) |  |  | 32 |  |  |  |  | This is a cost of 1.9 & 1.10
| Est Annual Utility Cost for FIM 1.1 - 1.11: |  |  | 84708.6249 |  |  |  |  | This is a cost of 1.9 & 1.10
1.12 | Digitize project records and equipment info in BAS
| Cost | 5000
1.13 | Check hydronic vavles and airside damper actuators | [7 empty] | Estimated potential savings
| Cost | 2500 | [6 empty] | Estimated potential savings
| 25% | Expected CHW load savings | [6 empty] | Estimated potential savings
| CHW savings |  |  | 0 |  |  |  |  | Estimated potential savings
| Expected payback (yr) |  |  | #DIV/0! |  |  |  |  | Estimated potential savings
| Est Annual Utility Cost for FIM 1.1 - 1.13: |  |  | 84708.6249 |  |  |  |  | Estimated potential savings
1.14 | Test duct system for leaks and seal ductwork | [7 empty] | Estimated potential savings
| Cost |  |  | 8000 |  |  |  |  | Estimated potential savings
| 25% | Expected fan power reduction | [6 empty] | Estimated potential savings
| Calc in CEP Utility cell AA11 | [7 empty] | Estimated potential savings
| Total Savings |  |  | 2000 |  |  |  |  | Estimated potential savings
| Expected payback (yr) |  |  | 4 |  |  |  |  | Estimated potential savings
| Est Annual Utility Cost for FIM 1.1 - 1.14: |  |  | 82708.6249 |  |  |  |  | Estimated potential savings
1.15 | Rebalance airside and hydronic HVAC system for BAS | [7 empty] | Estimated potential savings
| Cost | 500 | [6 empty] | Estimated potential savings
1.16 | Repair CHW piping at AHUs
| Cost | 5000
1.17 | Repair CHW pump CHWP-2
| Cost | 7500
1.18 | Install a bypass around CHWP on CHW supply side
| Cost | 2500
| Total Savings |  |  | 600
| Expected Payback (yr) |  |  | 5
1.19 | Convert Constant Volume CHWP to variable speed
| Cost | 5000
| Total Savings |  |  | 300
| Expected Payback (yr) |  |  | 17
1.2 | Convert 3-way CHW valves to 2-way w/ bypass
| Cost | 3000
1.21 | Implement dynamic CHW DP setpoint reset
| 5% | Expected % Savings
| Savings for reduced fan load |  |  | 30
1.22 | Re-zone HVAC system to match space use
| 3% | Expected CHW load savings
| 3% | Expected electric reheat savings
| CHW savings |  |  | 0
| Fan Power Savings |  |  | 165.75
| Total Savings |  |  | 165.75
FIMs 2.1 through 2.5 are calculating in the Lighting_Pivot tab.
3.1 | Seal around all penetrations of building envelope
| 2% | Expected CHW load savings
| 2% | Expected electric reheat savings
| CHW savings |  |  | 0
| Fan Power Savings |  |  | 110.5
| Total Savings |  |  | 110.5
4.1 | Impement utility service submeter and integrate BAS | [7 empty] | Yes
| Cost | 5000 | [6 empty] | Yes
4.2 | Floor Captain Policy to turn off lights
| 25% | Expected lighting savings (w/ no other FIM)
| Annual lighting expenses |  |  | 3226.1547
| Total lighting savings |  |  | 806.5387
4.3 | Reduce plug load through integrated controls | [7 empty] | Yes
| 25% | Expected Annual Savings | [6 empty] | Yes
| Annual plug load (non-computer) expenses |  |  | 3000 |  |  |  |  | Yes
| Total plug load savings |  |  | 750 |  |  |  |  | Yes
4.4 | Reduce computer load through IT power management | [7 empty] | Yes
| 25% | Expected Annual Savings | [6 empty] | Yes
| Annual plug load (non-computer) expenses |  |  | 900 |  | Let |  |  | Yes
| Total plug load savings |  |  | 225 |  |  |  |  | Yes
4.5
Note on C10: Imane El Ghazouani: Price Taken from RSMeans

## Elec Utility (kWh)
| Start Date (Required) | End Date (Required) | Usage (Required) | Cost (Optional) | Estimation (Required) | Avg Use/Day kWh | Unit Cost | kBtu/Mnth
Rows B through F may be used to import into EnergyStar® or BuildingEQ® | 4304000% | 4307000% | 97900 | 10309.08 | No | 3263.3333 | 0.1053 | 334048.6659
| 4300900% | 4304000% | 88100 | 9260.5 | No | 2841.9355 | 0.10511 | 300609.6779 | Max Daily kWh 2017 | Sum of Most Recent Year $ | Sum of most Recent Year kWh | total kBtu | kbtu/ft2
| 4297900% | 4300900% | 77200 | 8092.84 | No | 2573.3333 | 0.10483 | 263417.3341 | 4442.6667 | 114347.76 | 1075700 | 9392213.2097 | 154.4543
| 4294800% | 4297900% | 80800 | 8526.32 | No | 2606.4516 | 0.10552 | 275701.044 | Min Daily kWh 2017
| 4291700% | 4294800% | 80000 | 8466 | No | 2580.6452 | 0.10583 | 272971.3307 | 2573.3333 | Unit Cost Average (Most Recent Year)
| 4288700% | 4291700% | 77700 | 8207.35 | No | 2590 | 0.10563 | 265123.4049 | Est. Max Demand kW |  | 0.10661
| 4285600% | 4288700% | 79800 | 9889.24 | No | 2574.1935 | 0.12393 | 272288.9023 | 185.1111
| 4282600% | 4285600% | 83400 | 8917.12 | No | 2780 | 0.10692 | 284572.6122 | With Correction Factor (kW) | 28511 | 29651.44
| 4279500% | 4282600% | 97700 | 10141.49 | No | 3151.6129 | 0.1038 | 333366.2376 | 240 |  | 1140.44
| 4276700% | 4279500% | 91700 | 10078.66 | No | 3275 | 0.10991 | 312893.3878 | Summed kBtu 2017
| 4273600% | 4276700% | 113800 | 12141.08 | No | 3670.9677 | 0.10669 | 388301.7178 | 3670440.7548 | Row Labels | Sum of Usage (Required) | Sum of Cost (Optional)
| 4270500% | 4273600% | 107600 | 10318.08 | No | 3470.9677 | 0.095893 | 367146.4397 | 60.3602 | 4167500% | 39610 | 3971.45
| 4267500% | 4270500% | 99100 | 8919.09 | No | 3303.3333 | 0.090001 | 338143.2358 |  | 4170300% | 34210 | 3450.53
| 4264400% | 4267500% | 89800 | 8298.54 | No | 2896.7742 | 0.092411 | 306410.3187 |  | 4173300% | 33940 | 3332.06
| 4261400% | 4264400% | 86300 | 7362.76 | No | 2876.6667 | 0.085316 | 294467.8229 | 113800 | 4176500% | 31820 | 3228.88
| 4258300% | 4261400% | 88100 | 7806.85 | No | 2841.9355 | 0.088614 | 300609.6779 |  | 4179400% | 24290 | 2449.91
| 4255200% | 4258300% | 85700 | 7371.63 | No | 2764.5161 | 0.086017 | 292420.538 |  | 4182300% | 23800 | 2401.5
| 4252200% | 4255200% | 77200 | 6942.56 | No | 2573.3333 | 0.08993 | 263417.3341 |  | 4185800% | 29090 | 2900.88
| 4249100% | 4252200% | 74900 | 6743.51 | No | 2416.129 | 0.090034 | 255569.4083 |  | 4188700% | 20750 | 2048.28
| 4246100% | 4249100% | 78800 | 6944.4 | No | 2626.6667 | 0.088127 | 268876.7607 |  | 4191200% | 20130 | 2193.9
| 4243000% | 4246100% | 87600 | 7710.04 | No | 2825.8065 | 0.088014 | 298903.6071 |  | 4191800% | 5280 | 562.32
| 4240100% | 4243000% | 100100 | 9729.71 | No | 3451.7241 | 0.0972 | 341555.3775 |  | 4194900% | 28800 | 2970.38
| 4237100% | 4240100% | 113300 | 10739.51 | No | 3776.6667 | 0.094788 | 386595.647 |  | 4197800% | 32680 | 3269.04
| 4234000% | 4237100% | 93600 | 8183.9 | No | 3019.3548 | 0.087435 | 319376.4569 |  | 4201200% | 39560 | 3998.15
| 4231000% | 4234000% | 87700 | 8521.88 | No | 2923.3333 | 0.097171 | 299244.8212 |  | 4204100% | 36720 | 3648.62
| 4228100% | 4231000% | 82600 | 8268.76 | No | 2848.2759 | 0.10011 | 281842.8989 |  | 4206800% | 32200 | 3308.7
| 4225000% | 4228100% | 86800 | 8747.42 | No | 2800 | 0.10078 | 296173.8938 |  | 4210200% | 30520 | 3123.42
| 4222000% | 4225000% | 82200 | 8360.48 | No | 2740 | 0.10171 | 280478.0422 |  | 4213000% | 22440 | 2314.26
| 4219300% | 4222000% | 74200 | 7039.7 | No | 2748.1481 | 0.094875 | 253180.9092 |  | 4216300% | 23080 | 2300.36
| 4216300% | 4219300% | 83000 | 8374.96 | No | 2766.6667 | 0.1009 | 283207.7555 |  | 4219300% | 19040 | 1959.77
| 4213000% | 4216300% | 95100 | 9322.31 | No | 2881.8182 | 0.098026 | 324494.6693 |  | 4222000% | 17640 | 1711.75
| 4210200% | 4213000% | 84500 | 8576.11 | No | 3017.8571 | 0.10149 | 288325.968 |  | 4225100% | 19840 | 2055.88
| 4206800% | 4210200% | 109500 | 11076.71 | No | 3220.5882 | 0.10116 | 373629.5088 |  | 4228300% | 21000 | 2154.26
| 4204000% | 4206800% | 102600 | 10433.18 | No | 3664.2857 | 0.10169 | 350085.7316 |  | 4231000% | 21240 | 2163.44
| 4201200% | 4204000% | 113300 | 11153.46 | No | 4046.4286 | 0.098442 | 386595.647 |  | 4234000% | 25120 | 2476.65
| 4197800% | 4201200% | 129000 | 12924.26 | No | 3794.1176 | 0.10019 | 440166.2707 |  | 4237100% | 28040 | 2486.74
| 4194800% | 4197800% | 114600 | 11338.16 | No | 3820 | 0.098937 | 391031.4312 |  | 4240100% | 36800 | 3494.96
| 4191500% | 4194800% | 106200 | 10818.74 | No | 3218.1818 | 0.10187 | 362369.4414 |  | 4243000% | 32400 | 3156.04
| 4188700% | 4191500% | 84500 | 9049.31 | No | 3017.8571 | 0.10709 | 288325.968 |  | 4246100% | 28240 | 2492.3
| 4185700% | 4188700% | 86000 | 8331.86 | No | 2866.6667 | 0.096882 | 293444.1804 |  | 4249100% | 24760 | 2188.88
| 4182300% | 4185700% | 98800 | 9732.46 | No | 2905.8824 | 0.098507 | 337119.5934 |  | 4252200% | 22920 | 2070.51
| 4179400% | 4182300% | 85200 | 8467.82 | No | 2937.931 | 0.099388 | 290714.4671 |  | 4255200% | 18760 | 1694.65
| 4176400% | 4179400% | 85500 | 8497.46 | No | 2850 | 0.099385 | 291738.1096 |  | 4258300% | 17880 | 1545.89
| 4173300% | 4176400% | 96200 | 9660.44 | No | 3103.2258 | 0.10042 | 328248.0251 |  | 4261400% | 18520 | 1649.02
| 4171100% | 4173300% | 78500 | 7590.95 | No | 3568.1818 | 0.0967 | 267853.1182 |  | 4264400% | 20200 | 1731.04
| 4170300% | 4171100% | 28960 | 2850.49 | No | 3620 | 0.098429 | 98815.6217 |  | 4267500% | 25360 | 2350.73
| 4167500% | 4170300% | 109920 | 10976.11 | No | 3925.7143 | 0.099855 | 375062.6083 |  | 4270500% | 29120 | 2627.89
| 4164500% | 4167500% | 133280 | 13244.78 | No | 4442.6667 | 0.099376 | 454770.2369 |  | 4273600% | 29280 | 2815.02
| 4161200% | 4164500% | 127760 | 12008.4 | No | 3871.5152 | 0.093992 | 435935.215 |  | 4276700% | 33840 | 3617.34
[10 empty] | 4279500% | 27760 | 3058.05
[10 empty] | 4282600% | 30400 | 3162.48
[10 empty] | 4285600% | 25040 | 2684.27
[10 empty] | 4288700% | 23920 | 2971.3
[10 empty] | 4291700% | 22680 | 2402.74
[10 empty] | 4294800% | 21200 | 2250.84
[10 empty] | 4297900% | 20000 | 2118
[10 empty] | 4300900% | 21240 | 2233.83
[10 empty] | 4304000% | 25360 | 2672.8
[10 empty] | 4307000% | 25160 | 2656.83
[10 empty] | Grand Total | 1241680 | 124126.54

## CEP Utility (Tons)
|  |  | tons | $
| Start Date (Required) | End Date (Required) | Usage (Required) | Cost (Optional) | Estimation (Required) | Use/Day | Unit Cost | Demand kWh/mnth | (kBtu/h)/mnth | Billing Period | kW Demand | kBtu
Rows B through F may be used to import into EnergyStar® or BuildingEQ® | 4304200% | 4307300% | 15917 | 2797.07 | No | 513.4516 | 0.17573 | 55977.7015 | 191004000 | 31 | 75.2388 | 256725.8065
| 4300900% | 4304200% | 22337 | 3921.21 | No | 676.8788 | 0.17555 | 78555.8784 | 268044000 | 33 | 99.1867 | 338439.3939 |  | Sum of Most Recent Year $ | Sum of most Recent Year tons*hr | Annual kWh | kBtu | Annual $ CEP Elec
| 4298000% | 4300900% | 37886 | 6643.84 | No | 1306.4138 | 0.17536 | 133239.3791 | 454632000 | 29 | 191.4359 | 653206.8966 |  | 56501.81 | 348500 | 1225622.225 | 5721772.455 | 170849.57
| 4294900% | 4298000% | 42503 | 7452.28 | No | 1371.0645 | 0.17534 | 149476.6755 | 510036000 | 31 | 200.9095 | 685532.2581 |  |  |  | .78 kw/ton CEP |  |  | Hanson | UCF's OEIS
| 4291800% | 4294900% | 42281 | 7413.4 | No | 1363.9032 | 0.17534 | 148695.9348 | 507372000 | 31 | 199.8601 | 681951.6129 |  | Unit Cost Average (Most Recent Year) |  | kW | kWh | kBtu | kBtu/sqft | kbtu/sqft
| 4288800% | 4291800% | 37397 | 6558.21 | No | 1246.5667 | 0.17537 | 131519.6394 | 448764000 | 30 | 182.6662 | 623283.3333 |  | 0.16005 |  | 271830 | 1227822.1313 | 4189503.0121 | 68.8961 | 68.8 | CHW
| 4285600% | 4288800% | 35846 | 5178.99 | No | 1120.1875 | 0.14448 | 126065.0051 | 430152000 | 32 | 164.1471 | 560093.75 | [7 empty] | 59.6 | Elec
| 4282700% | 4285600% | 30205 | 4365.56 | No | 1041.5517 | 0.14453 | 106226.4542 | 362460000 | 29 | 152.6242 | 520775.8621 |  | 1175 | mbh | Summed kBtu |  |  |  | 53.58% | % CHW
The data should have the most recent billing period at the top and the oldest billing period at the bottom of the table. | 4279500% | 4282700% | 29515 | 4266.06 | No | 922.3438 | 0.14454 | 103799.8277 | 354180000 | 32 | 135.156 | 461171.875 | Max kBtu/h/yr | 10293000 | % of Max | 7859943.7669 |  |  |  | 46.42% | % Elec
| 4276800% | 4279500% | 25353 | 3665.9 | No | 939 | 0.14459 | 89162.698 | 304236000 | 27 | 137.5968 | 469500 |  |  | 76.36% |  | Lighting CHW Demand (kW) |  | 14.82
| 4273800% | 4276800% | 13348 | 1934.78 | No | 444.9333 | 0.14495 | 46942.9138 | 160176000 | 30 | 65.1985 | 222466.6667 |  |  |  |  | Est. Lighting CHW (kWh/yr) |  | 129823.2
| 4270600% | 4273800% | 15912 | 2304.51 | No | 497.25 | 0.14483 | 55960.1172 | 190944000 | 32 | 72.8647 | 248625 |  |  |  |  | Lighting kWh/Total CHW kWh |  | 10.57%
| 4267600% | 4270600% | 13851 | 2007.31 | No | 461.7 | 0.14492 | 48711.8893 | 166212000 | 30 | 67.6554 | 230850 |  | Row Labels | Sum of Usage (Required) | Sum of Cost (Optional)
| 4264500% | 4267600% | 20634 | 2985.42 | No | 665.6129 | 0.14468 | 72566.6829 | 247608000 | 31 | 97.5359 | 332806.4516 |  | 4167500% | 7795 | 993.14
| 4261500% | 4264500% | 42599 | 6152.78 | No | 1419.9667 | 0.14443 | 149814.2931 | 511188000 | 30 | 208.0754 | 709983.3333 |  | 4170300% | 7738 | 986.24
| 4258400% | 4261500% | 44317 | 6400.51 | No | 1429.5806 | 0.14443 | 155856.2415 | 531804000 | 31 | 209.4842 | 714790.3226 |  | 4173300% | 8963 | 1134.46
| 4255300% | 4258400% | 45879 | 6625.75 | No | 1479.9677 | 0.14442 | 161349.5611 | 550548000 | 31 | 216.8677 | 739983.871 |  | 4176500% | 10997 | 1380.58
| 4252400% | 4255300% | 35483 | 5126.65 | No | 1223.5517 | 0.14448 | 124788.3885 | 425796000 | 29 | 179.2937 | 611775.8621 |  | 4179400% | 9709 | 1224.73
| 4249400% | 4252400% | 39360 | 4843.41 | No | 1312 | 0.12305 | 138423.216 | 472320000 | 30 | 192.2545 | 656000 |  | 4182300% | 10642 | 1337.62
| 4246600% | 4249400% | 34860 | 4290.81 | No | 1245 | 0.12309 | 122597.391 | 418320000 | 28 | 182.4366 | 622500 |  | 4185800% | 13504 | 1683.92
| 4246600% | 4249400% | -12251 | -1514.42 | No | -437.5357 | 0.12362 | -43084.9293 | -147012000 | 28 | -64.1145 | -218767.8571 |  | 4188700% | 9892 | 1246.87
| 4246600% | 4249400% | 12251 | 1514.42 | No | 437.5357 | 0.12362 | 43084.9293 | 147012000 | 28 | 64.1145 | 218767.8571 |  | 4191800% | 10139 | 1276.76
| 4243300% | 4246600% | 35970 | 4427.12 | No | 1090 | 0.12308 | 126501.0945 | 431640000 | 33 | 159.7236 | 545000 |  | 4194900% | 8544 | 1083.76
| 4243300% | 4246600% | 13772 | 1701.2 | No | 417.3333 | 0.12353 | 48434.0582 | 165264000 | 33 | 61.1541 | 208666.6667 |  | 4197800% | 7417 | 947.4
| 4243300% | 4246600% | -13772 | -1701.2 | No | -417.3333 | 0.12353 | -48434.0582 | -165264000 | 33 | -61.1541 | -208666.6667 |  | 4201200% | 8621 | 1093.08
| 4240400% | 4243300% | 27376 | 3371.77 | No | 944 | 0.12317 | 96277.2856 | 328512000 | 29 | 138.3294 | 472000 |  | 4204100% | 6479 | 833.9
| 4240400% | 4243300% | -11772 | -1455.6 | No | -405.931 | 0.12365 | -41400.3582 | -141264000 | 29 | -59.4833 | -202965.5172 |  | 4206800% | 5993 | 775.09
| 4240400% | 4243300% | 11772 | 1455.6 | No | 405.931 | 0.12365 | 41400.3582 | 141264000 | 29 | 59.4833 | 202965.5172 |  | 4210200% | 7791 | 992.65
| 4237200% | 4240400% | 19519 | 2406.93 | No | 609.9688 | 0.12331 | 68645.3951 | 234228000 | 32 | 89.382 | 304984.375 |  | 4212100% | 5301 | 691.36
| 4234200% | 4237200% | 28287 | 3501.73 | No | 942.9 | 0.12379 | 99481.1359 | 339444000 | 30 | 138.1682 | 471450 |  | 4213000% | 2669 | 322.95
| 4231100% | 4234200% | 32699 | 4035.58 | No | 1054.8065 | 0.12342 | 114997.4781 | 392388000 | 31 | 154.5665 | 527403.2258 |  | 4216300% | 9557 | 1206.34
| 4228100% | 4231100% | 37922 | 4667.56 | No | 1264.0667 | 0.12308 | 133365.9857 | 455064000 | 30 | 185.2305 | 632033.3333 |  | 4219300% | 9543 | 1204.64
| 4225000% | 4228100% | 49124 | 6023 | No | 1584.6452 | 0.12261 | 172761.7394 | 589488000 | 31 | 232.2066 | 792322.5806 |  | 4222000% | 8981 | 1165.7
| 4222000% | 4225000% | 48814 | 5985.49 | No | 1627.1333 | 0.12262 | 171671.5159 | 585768000 | 30 | 238.4327 | 813566.6667 |  | 4225100% | 10407 | 1338.25
| 4219300% | 4222000% | 43001 | 5282.12 | No | 1592.6296 | 0.12284 | 151228.0669 | 516012000 | 27 | 233.3766 | 796314.8148 |  | 4228300% | 9972 | 1285.61
| 4216300% | 4219300% | 48103 | 5870.4 | No | 1603.4333 | 0.12204 | 169171.0356 | 577236000 | 30 | 234.9598 | 801716.6667 |  | 4231100% | 8035 | 1051.24
| 4213000% | 4216300% | 48127 | 5873.31 | No | 1458.3939 | 0.12204 | 169255.4399 | 577524000 | 33 | 213.7064 | 729196.9697 |  | 4234200% | 8214 | 1072.89
| 4210200% | 4213000% | 39753 | 4860.05 | No | 1419.75 | 0.12226 | 139805.338 | 477036000 | 28 | 208.0437 | 709875 |  | 4237200% | 8015 | 1048.82
| 4206800% | 4210200% | 41802 | 5107.98 | No | 1229.4706 | 0.12219 | 147011.3637 | 501624000 | 34 | 180.161 | 614735.2941 |  | 4240500% | 7224 | 897.11
| 4204000% | 4206800% | 26145 | 3213.48 | No | 933.75 | 0.12291 | 91948.0432 | 313740000 | 28 | 136.8274 | 466875 |  | 4243300% | 5836 | 726.66
| 4201300% | 4204000% | 20210 | 2495.35 | No | 748.5185 | 0.12347 | 71075.5385 | 242520000 | 27 | 109.6845 | 374259.2593 |  | 4246600% | 8313 | 1030.84
| 4197800% | 4201300% | 29750 | 3649.69 | No | 850 | 0.12268 | 104626.2875 | 357000000 | 35 | 124.5551 | 425000 |  | 4249300% | 6840 | 849.95
| 4194800% | 4197800% | 28410 | 3487.55 | No | 947 | 0.12276 | 99913.7085 | 340920000 | 30 | 138.769 | 473500 |  | 4252400% | 8223 | 1019.78
| 4191500% | 4194800% | 17819 | 2206.04 | No | 539.9697 | 0.1238 | 62666.7501 | 213828000 | 33 | 79.1247 | 269984.8485 |  | 4255400% | 9049 | 1314.87
| 4188700% | 4191500% | 19572 | 2418.15 | No | 699 | 0.12355 | 68831.7882 | 234864000 | 28 | 102.4283 | 349500 |  | 4258400% | 9313 | 1352.93
| 4185700% | 4188700% | 30449 | 3734.27 | No | 1014.9667 | 0.12264 | 107084.5656 | 365388000 | 30 | 148.7286 | 507483.3333 |  | 4261400% | 9306 | 1351.93
| 4182300% | 4185700% | 52145 | 6359.48 | No | 1533.6765 | 0.12196 | 183386.1432 | 625740000 | 34 | 224.7379 | 766838.2353 |  | 4264500% | 9451 | 1372.83
| 4179400% | 4182300% | 38352 | 4690.53 | No | 1322.4828 | 0.1223 | 134878.2312 | 460224000 | 29 | 193.7906 | 661241.3793 |  | 4267500% | 8373 | 1217.39
| 4176400% | 4179400% | 34994 | 4284.21 | No | 1166.4667 | 0.12243 | 123068.6489 | 419928000 | 30 | 170.9287 | 583233.3333 |  | 4270600% | 7160 | 1042.47
| 4173300% | 4176400% | 33228 | 4070.53 | No | 1071.871 | 0.1225 | 116857.8918 | 398736000 | 31 | 157.0671 | 535935.4839 |  | 4273800% | 7825 | 1138.36
| 4170300% | 4173300% | 28552 | 3504.73 | No | 951.7333 | 0.12275 | 100413.1012 | 342624000 | 30 | 139.4626 | 475866.6667 |  | 4276800% | 6646 | 968.35
| 4167500% | 4170300% | 26724 | 3283.54 | No | 954.4286 | 0.12287 | 93984.2994 | 320688000 | 28 | 139.8576 | 477214.2857 |  | 4279500% | 6417 | 935.33
| 4164500% | 4167500% | 28552 | 3504.73 | No | 951.7333 | 0.12275 | 100413.1012 | 342624000 | 30 | 139.4626 | 475866.6667 |  | 4282600% | 7179 | 1045.21
[14 empty] | 4285700% | 7683 | 1117.89
[14 empty] | 4288800% | 8525 | 1239.3
[14 empty] | 4291800% | 9009 | 1587.48
[14 empty] | 4294900% | 9405 | 1656.82
[14 empty] | 4298000% | 9636 | 1697.26
[14 empty] | 4300900% | 8837 | 1557.36
[14 empty] | 4304200% | 8915 | 1571.02
[14 empty] | 4307000% | 5829 | 1030.66
[14 empty] | Grand Total | 399912 | 55099.8

## Schedule-Building Info
Building Address
4336 Scorpius Street | [12 empty] | GHG (Portfolio Manager)
Orlando | FL | 32816 | [6 empty] | Sanity check |  |  |  | Total GHG Emissions Intensity (kgCO2e/ft²) | 12.3
[9 empty] | Occupants/1000ft2 |  | CFM/Person | ASHRAE Estimated CFM | Sq. Ft. | 60809
ASHRAE Ventilation Space Type: |  |  | Lecture classroom |  | # of Floors | Surface Area |  |  | 65 |  | 65 | 256918.025 | Total GHG Emissions (kgCO2e) | 747950.7
ft2 | 60809 | Perimeter 1 |  | Height 1 |  | 0 |  | FTE/1000ft2 | Actual compared to 62.1 Minimum Standard
FTE | 653 | Perimeter 2 |  | Height 2 |  | 0 |  | 10.7385 | 16.52% |  |  | 16.52%
Build Yr | 2003 | Perimeter 3 |  | Height 3
[5 empty] | Total: | 0
Scheduled Run time for Mech
Mon-Friday | 24 | hrs |  |  |  |  | Augment Sch hrs/yr by % |  |  | Augmeted Sch hrs/yr |  | If you need to have a piece of equipment run year around change the Utilization % to the below quantity.
Sat-Sun | 24 | hrs | 8760 |  |  |  | 100% |  |  | 8760
100% Assumes no holidays which should lead to high estimates.
Occupancy Schedule
Mon-Friday | 15 | hrs
Sat-Sun | 15 | hrs | 5475 |  |  |  | 100% |  |  | 5475 |  | 160%
Augmented Avg Hr/day
Weekly Operating Hours | [9 empty] | 15
Mech | 168 | For EP
Occ | 105 | 136.5
105
Scratch Pad 1.
Elevator Run Time Thought Process.
Classes 1.5 hr each on average.
Elevators utilized most frequently between classes.
(12hrs occupancy a day)/(1.5 hrs for a class) =
8 | class periods per day.
The period between classes elevators are used more frequently for 15min
8 breaks at 15 min each: |  |  | 120 | min
Or 2 hrs of heavy elevator use/day
Yielding a utilization factor of: |  |  | 16.67%

## VAV wLowCFM
This only represents VTU's with obvious disparities.
Total VTU's | 25
VTU | Room # | Design CFM | Tested CFM | % Diff
1B-5 | 105J | 165 | 82 | 49.7%
1B-8 | 101Z | 20 | 177 | 885%
1B-9 | 107Z | 150 | 69 | 46%
1B-11 | 111 | 100 | 2 | 2%
1B-12 | 100 | 250 | 148 | 59.2%
1B-13 | 106F | 180 | 99 | 55%
1B-14 | 106B | 180 | 0 | 0%
1C-1 | 109H | 160 | 77 | 48.12%
1C-1 | 114 | ? | 2 | #VALUE!
1C-2 | 109G | 220 | 135 | 61.36%
1C-3 | 115E | 130 | 0 | 0%
1C-9 | 109D | 125 | 24 | 19.2%
1C-10 | 108 | 240 | 47 | 19.58%
1C-11 | 105B | 400 | 180 | 45%
1C-11 | 105 | 285 | 152 | 53.33%
1C-12 | 113 | 450 | 296 | 65.78%
13
2.5

## Spec Wattages
Title | Spec Wattage | Archived
AHU |  | Mechanical
Audio And Visual | 120 | Plug Load
Audio Visual | 120 | Plug Load
Break Room | 230 | Plug Load
Coffee | 1000 | Plug Load
Conference Room | 230 | Plug Load
Desktop | 50 | Plug Load
Desktop + Monitor | 71 | Plug Load
Fan | 30 | Fan
Laptop | 40 | Plug Load
LED | 12 | Lighting
LEDs | 12 | Lighting
Light Fixture |  | Lighting
Lighting Control |  | Lighting
Lighting Fixture |  | Lighting
Microwave | 1200 | Plug Load
Minifridge | 57 | Plug Load
Monitor | 21 | Plug Load
Phone | 5 | Plug Load
Printer | 100 | Plug Load
Projector | 308 | Plug Load
Refrigerator | 408 | Plug Load
Refrigerator | 57 | Plug Load
Shredder | 265 | Plug Load
Space Heater | 750 | Plug Load
Storage |  | Misc
Television | 175 | Plug Load
Transformer |  | Electrical
Typical Cube | 150 | Plug Load
Typical Office | 237 | Plug Load
UPS | 276 | Plug Load
Water Fountain | 370 | Plug Load

## 62.1_2013_Table6.2.2.1
ASHRAE 62.1 Table 6.2.2.1 - 2013 | People Outdoor Air Rate |  | Area Outdoor Air Rate |  | Occupant Density | Combined Outdoor Air Rate
| cfm/person | L/s*person | cfm/ft2 | L/s*m2 | #/1000ft2 | cfm/person | L/s*person
Cell | 5 | 2.5 | 0.12 | 0.6 | 25 | 10 | 4.9 | 2
Dayroom | 5 | 2.5 | 0.06 | 0.3 | 30 | 7 | 3.5 | 1
Guard stations | 5 | 2.5 | 0.06 | 0.3 | 15 | 9 | 4.5 | 1
Booking/waiting | 7.5 | 3.8 | 0.06 | 0.3 | 50 | 9 | 4.4 | 2
Daycare (through age 4) | 10 | 5 | 0.18 | 0.9 | 25 | 17 | 8.6 | 2
Daycare sickroom | 10 | 5 | 0.18 | 0.9 | 25 | 17 | 8.6 | 3
Classrooms (ages 5–8) | 10 | 5 | 0.12 | 0.6 | 25 | 15 | 7.4 | 1
Classrooms (age 9 plus) | 10 | 5 | 0.12 | 0.6 | 35 | 13 | 6.7 | 1
Lecture classroom | 7.5 | 3.8 | 0.06 | 0.3 | 65 | 8 | 4.3 | 1
Lecture hall (fixed seats) | 7.5 | 3.8 | 0.06 | 0.3 | 150 | 8 | 4 | 1
Art classroom | 10 | 5 | 0.18 | 0.9 | 20 | 19 | 9.5 | 2
Science laboratories | 10 | 5 | 0.18 | 0.9 | 25 | 17 | 8.6 | 2
Wood/metal shop | 10 | 5 | 0.18 | 0.9 | 20 | 19 | 9.5 | 2
Computer lab | 10 | 5 | 0.12 | 0.6 | 25 | 15 | 7.4 | 1
Media center | 10 | 5 | 0.12 | 0.6 | 25 | 15 | 7.4 | 1
Music/theater/dance | 10 | 5 | 0.06 | 0.3 | 35 | 12 | 5.9 | 1
Multiuse assembly | 7.5 | 3.8 | 0.06 | 0.3 | 100 | 8 | 4.1 | 1
Restaurant dining rooms | 7.5 | 3.8 | 0.18 | 0.9 | 70 | 10 | 5.1 | 2
Cafeteria/fast-food dining | 7.5 | 3.8 | 0.18 | 0.9 | 100 | 9 | 4.7 | 2
Bars, cocktail lounges | 7.5 | 3.8 | 0.18 | 0.9 | 100 | 9 | 4.7 | 2
Kitchen (cooking) | 7.5 | 3.8 | 0.12 | 0.6 | 20 | 14 | 7 | 2
Break rooms | 5 | 2.5 | 0.06 | 0.3 | 25 | 7 | 3.5 | 1
Coffee stations | 5 | 2.5 | 0.06 | 0.3 | 20 | 8 | 4 | 1
Conference/meeting | 5 | 2.5 | 0.06 | 0.3 | 50 | 6 | 3.1 | 1
Corridors | - | — | 0.06 | 0.3 | — |  |  | 1
Occupiable storage rooms for liquids or gels | 5 | 2.5 | 0.12 | 0.6 | 2 | 65 | 32.5 | 2
Bedroom/living room | 5 | 2.5 | 0.06 | 0.3 | 10 | 11 | 5.5 | 1
Barracks sleeping areas | 5 | 2.5 | 0.06 | 0.3 | 20 | 8 | 4 | 1
Laundry rooms, central | 5 | 2.5 | 0.12 | 0.6 | 10 | 17 | 8.5 | 2
Laundry rooms within dwelling units | 5 | 2.5 | 0.12 | 0.6 | 10 | 17 | 8.5 | 1
Lobbies/prefunction | 7.5 | 3.8 | 0.06 | 0.3 | 30 | 10 | 4.8 | 1
Multipurpose assembly | 5 | 2.5 | 0.06 | 0.3 | 120 | 6 | 2.8 | 1
Breakrooms | 5 | 2.5 | 0.12 | 0.6 | 50 | 7 | 3.5 | 1
Main entry lobbies | 5 | 2.5 | 0.06 | 0.3 | 10 | 11 | 5.5 | 1
Occupiable storage rooms for dry materials | 5 | 2.5 | 0.06 | 0.3 | 2 | 35 | 17.5 | 1
Office space | 5 | 2.5 | 0.06 | 0.3 | 5 | 17 | 8.5 | 1
Reception areas | 5 | 2.5 | 0.06 | 0.3 | 30 | 7 | 3.5 | 1
Telephone/data entry | 5 | 2.5 | 0.06 | 0.3 | 60 | 6 | 3 | 1
Bank vaults/safe deposit | 5 | 2.5 | 0.06 | 0.3 | 5 | 17 | 8.5 | 2
Banks or bank lobbies | 7.5 | 3.8 | 0.06 | 0.3 | 15 | 12 | 6 | 1
Computer (not printing) | 5 | 2.5 | 0.06 | 0.3 | 4 | 20 | 10 | 1
Freezer and refrigerated spaces (<50°F) | 10 | 5 | 0 | 0 | 0 | 0 | 0 | 2
General manufacturing (excludes heavy industrial and processes using chemicals) | 10 | 5 | 0.18 | 0.9 | 7 | 36 | 18 | 3
Pharmacy (prep. area) | 5 | 2.5 | 0.18 | 0.9 | 10 | 23 | 11.5 | 2
Photo studios | 5 | 2.5 | 0.12 | 0.6 | 10 | 17 | 8.5 | 1
Shipping/receiving | 10 | 5 | 0.12 | 0.6 | 2 | 70 | 35 | 2
Sorting, packing, light assembly | 7.5 | 3.8 | 0.12 | 0.6 | 7 | 25 | 12.5 | 2
Telephone closets | - | — | 0 | 0 | — |  |  | 1
Transportation waiting | 7.5 | 3.8 | 0.06 | 0.3 | 100 | 8 | 4.1 | 1
Warehouses | 10 | 5 | 0.06 | 0.3 | — |  |  | 2
Auditorium seating area | 5 | 2.5 | 0.06 | 0.3 | 150 | 5 | 2.7 | 1
Places of religious worship | 5 | 2.5 | 0.06 | 0.3 | 120 | 6 | 2.8 | 1
Courtrooms | 5 | 2.5 | 0.06 | 0.3 | 70 | 6 | 2.9 | 1
Legislative chambers | 5 | 2.5 | 0.06 | 0.3 | 50 | 6 | 3.1 | 1
Libraries | 5 | 2.5 | 0.12 | 0.6 | 10 | 17 | 8.5 | 1
Lobbies | 5 | 2.5 | 0.06 | 0.3 | 150 | 5 | 2.7 | 1
Museums (children’s) | 7.5 | 3.8 | 0.12 | 0.6 | 40 | 11 | 5.3 | 1
Museums/galleries | 7.5 | 3.8 | 0.06 | 0.3 | 40 | 9 | 4.6 | 1
Dwelling unit | 5 | 2.5 | 0.06 | 0.3 |  |  |  | 1
Common corridors | - | — | 0.06 | 0.3 |  |  |  | 1
Sales (except as below) | 7.5 | 3.8 | 0.12 | 0.6 | 15 | 16 | 7.8 | 2
Mall common areas | 7.5 | 3.8 | 0.06 | 0.3 | 40 | 9 | 4.6 | 1
Barbershop | 7.5 | 3.8 | 0.06 | 0.3 | 25 | 10 | 5 | 2
Beauty and nail salons | 20 | 10 | 0.12 | 0.6 | 25 | 25 | 12.4 | 2
Pet shops (animal areas) | 7.5 | 3.8 | 0.18 | 0.9 | 10 | 26 | 12.8 | 2
Supermarket | 7.5 | 3.8 | 0.06 | 0.3 | 8 | 15 | 7.6 | 1
Coin-operated laundries | 7.5 | 3.8 | 0.12 | 0.6 | 20 | 14 | 7 | 2
Gym, sports arena (play area) | 20 | 10 | 0.18 | 0.9 | 7 | 45 | 23 | 2
Spectator areas | 7.5 | 3.8 | 0.06 | 0.3 | 150 | 8 | 4 | 1
Swimming (pool & deck) |  |  | 0.48 | 2.4 |  |  |  | 2
Disco/dance floors | 20 | 10 | 0.06 | 0.3 | 100 | 21 | 10.3 | 2
Health club/aerobics room | 20 | 10 | 0.06 | 0.3 | 40 | 22 | 10.8 | 2
Health club/weight rooms | 20 | 10 | 0.06 | 0.3 | 10 | 26 | 13 | 2
Bowling alley (seating | 10 | 5 | 0.12 | 0.6 | 40 | 13 | 6.5 | 1
Gambling casinos | 7.5 | 3.8 | 0.18 | 0.9 | 120 | 9 | 4.6 | 1
Game arcades | 7.5 | 3.8 | 0.18 | 0.9 | 20 | 17 | 8.3 | 1
Stages, studios | 10 | 5 | 0.06 | 0.3 | 70 | 11 | 5.4 | 1