## tab1
PSYCHROMETRIC AND HEATING ANALYSIS
Project Name: |  | Hanson Professional Services - 2 story HVAC renovation
Project Number: |  | 06S1736P
System: |  | RTU-1
Engineer: |  | TEC
Date: |  | 2007-01-12
[DRAW-THRU] [BLOW-THRU] SYSTEM
1. Determine what is known.
Weather Data
| Supply |  | OA | Return | OA Temp From Location Selected for Load Calculation |  | Room Cooling Design
| CFM | %OA | CFM | CFM | db (F) | wb (F) | db (F) | wb (F) | %RH
| 11600 | 34.61% | 4015 | 7585 | 93 | 76 | 72 | --- | 50
1a. Calculate the supply fan BHP: ENTER THE ESTIMATED SUPPLY FAN TOTAL STATIC PRESSURE
| Supply | Estimated | Brake
| CFM | Total Static | Horse
|  | Pressure | Power
| 11600 | 4 | 11.2523 |  | * Brake horsepower = CFM * Total Static Pressure / (6,344 * Fan Efficiency (65%)
1b. Calculate the return fan BHP: ENTER THE ESTIMATED RETURN FAN TOTAL STATIC PRESSURE
| Return | Estimated | Brake
| CFM | Total Static | Horse
|  | Pressure | Power
| 10637 | 2.5 | 6.4489 |  | * Brake horsepower = CFM * Total Static Pressure / (6,344 * Fan Efficiency (65%)
| Fan BHP |  | Load BTUH |  | Airside |  | * Airside delta T from HCC-V (usually 17-20 deg F)
| Supply | Return | Sensible | Latent | Delta T*
| 11.2523 | 6.4489 | 188349 | 30574 | 17
2. Plot OA condition (Point A on chart).
3. Plot Room design dry bulb temperature condition (step #1).
4. Plot the UNIT discharge temperature at delta T distance (from step #1) from room design dry bulb temperature (step #3).
| Room |  | Unit
| Temp | Airside | Discharge
| db | delta T | Air Temp
| 72 | 17 | 55
5. Calculate supply fan heat delta T and draw a line delta T distance from UNIT supply air discharge condition Step #4. See table for fan BTUH.
| Supply | Supply | Coil
| Fan | Fan | Leaving
| BTUH | Delta T* | Air Temp
| 29900 | 2.3867 | 52.6133 |  | * Delta T = BTUH / (1.08 x CFM)
6. Plot the COIL discharge condition (Point B on chart) on the COIL leaving dry bulb temperature near the saturation line.
7. Determine h (leaving air).
| LAT |  | h
| db | wb | Leaving Air
| 52.6133 | 51 | 21.04
8. Draw a line from Point B straight across and meet with the UNIT discharge air dry bulb temperature to a new Point C.
9. Calculate SHR (sensible heat ratio ) = sensible load / (sensible + latent)
SHR
0.86034
9a. Draw a line through SHR and 78 deg F / 50% RH point.
9b. Draw a parallel line through the UNIT discharge condition Point C to the room dry bulb temperature and plot new Point D the room condition.
10. Verify that the room condition is within an acceptable humidity range (typically 40-60% relative humidity).
11. If the room condition is not within an acceptable humidity range:
a. Reduce delta T (results in possible higher total CFM).
b. Increase coil delta T (results in lower CFM) and add a Reheat coil in the unit.
c. Increase delta T (lowers total CFM, could reduce coil physical size and increase number of rows).
12. Calculate return fan and/or plenum heat delta T, and draw a line delta T distance from Point D to new point E. See Table for fan BTUH.
| Return | Return | Return | Return | Return | Return | Final
| Plen | Plen | Plen | Fan | Fan | Fan | Return
| CFM | BTUH | delta T* | CFM | BTUH | delta T* | Temp
| 10637 | 61406 | 5.3452 | 10637 | 19100 | 1.6626 | 79.0079 |  | * Delta T = BTUH / (1.08 x CFM)
13. Connect return air condition (Point E) and OA condition (Point A).
14. Calculate mixed air temp. MAT = (RA temp x %RA) + (OA temp x %OA)
| Return |  |  | OA |  |  | Mixed Air Temp
| Temp | %RA | + | Temp | %OA | = | db | wb* | * Plot to determine wet bulb.
| 79.0079 | 65.39% |  | 93 | 34.61% |  | 83.8508 | 68.2
15. Plot MAT (Point F) on line AC and determine h (ent air).
h
Entering Air
30.85
16. Calculate total load. Total Load = Total CFM x 4.45 x (h ent - h leav) = BTUH
| Supply |  | Delta h |  | Total |  | Total
| CFM |  | ent-leav |  | BTUH |  | Tons
| 11600 | x 4.45 x | 9.81 | = | 506390 | / 12000 = | 42.1992
17. Check figures.
| CFM / Ton = |  | 274.8869
HEATING COIL CALCULATION
1. Determine what is known.
| Supply |  | OA | Return | OA Temp |  | Heating Design
| CFM | %OA | CFM | CFM | db (F) | wb (F) | Return Air Temperature db (F) | Coil Design LAT | Space Heat Loss BTUH
Maximum | 0 | #DIV/0! | 4015 | -4015 | 0 | N/A | 72 | 55 | 0
Minimum | 0 | #DIV/0! | 4015 | -4015 | 0 | N/A | 72 | 55 | 0
2. Calculate mixed air temp. MAT = (RA temp x %RA) + (OA temp x %OA)
| Return |  |  | OA |  |  | Mixed Air Temp
| Temp | %RA | + | Temp | %OA | = | db | wb
Maximum | 72 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | N/A
Minimum | 72 | #DIV/0! |  | 0 | #DIV/0! |  | #DIV/0! | N/A
3. Calculate BTUh required for heating = (MAT - LAT)x CFM x 1.08 = BTUH | OA =: or 10 deg min.
| Air Temperature Rise Deg F | Design CFM | Coversion |  | Ventilation BTUH
Maximum | Return Temp: #DIV/0!; Return %RA: 0; Return +: 1.085; OA %OA: #DIV/0!
Minimum | Return Temp: #DIV/0!; Return %RA: 0; Return +: 1.085; OA %OA: #DIV/0!
4. Calculate total BTUH required for heating coil selection = Ventilation BTUH + Space Heat Loss BTUH * safety = Unit coil minimum required BTUH
| Ventilation BTUH | * | Safety Factor | + | Space Heat Loss BTUH | * | Safety Factor | = | Unit coil Min. Required BTUH
Maximum | Return Temp: #DIV/0!; Return +: 0; OA %OA: 0; Mixed Air Temp db: 0 | #DIV/0!
Minimum | Return Temp: #DIV/0!; Return +: 0; OA %OA: 0; Mixed Air Temp db: 0 | #DIV/0!
5. Re-calculate Leaving Air Temperature = Coil BTUH/(1.08 * CFM) = Air Temperaure Rise + MAT (use minimum 10 deg)
| Coil Min. Required BTUH | / | CFM*1.085 | = | Coil Discharge air Temp Deg F
Maximum | Return Temp: #DIV/0!; Return +: 0; OA %OA: #DIV/0!
Minimum | Return Temp: #DIV/0!; Return +: 0; OA %OA: #DIV/0!
Note on G142: If the coil DISCHARGE air temperature is 15 Deg F above the room temperature it may result in potentially poor heating. Increase airflow to reduce discharge air or add separate hydronic or electric perimeter heating device.
Note on G143: If the coil DISCHARGE air temperature is 15 Deg F above the room temperature it may result in potentially poor heating. Increase airflow to reduce discharge air or add separate hydronic or electric perimeter heating device.