## Sheet1
Column1 | Unnamed: 0 | Name | DeviceId | Device Tag | ipaddresses | Value | Units | Multiplier | State | IOU | Channel | filter_ip | Equip_Markers | Measurement_Marker | Measurement_Kind | Measurement_Unit_HayStack | Missing Points | Notes
0 | 0 | HWST | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | 106 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/boiler.xml | boiler, gas | his, point, writable, sensor | Number | fahrenheit |  | Not bringing in lights points: Light, Current Line, Tim Min, Ovrd Time, Area, Start Time, Stop Time
1 | 1 | HWRT | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | 104.5 | °F | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number | fahrenheit |  | Not bringing in Liebert units (1, 2) points: System Operating State (System Info), System Status (System Info), Return Air Temperature (System Operations), Air Temperature Set Point (Air), Return Dew Point (System Operations), Return Humidity (Humidity), Humidity Set Point (Humdity), Supply Air Temperature (System Operations), Compressor Hours (Compressors->Compressor[1]), Dehumidifier Hours (Dehumidifier), Fan Hours (Fan), Leibert 1 run enable, Leibert 2 run enable, Clogged Air Filter
2 | 2 | ReheatHWRT | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | 99.5 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit |  | Not bringing in Unit Heaters points: Vlv, RmT, StPt, VAV#
3 | 3 | BoilerAlrm | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | Off |  | 1 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Bool |  |  | Not bringing in FinTube: RmT, Heat StPt, Fintube,
4 | 4 | Pmp1Prv | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | On |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool
5 | 5 | Pmp2Prv | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | Off |  | 1 | Enabled | 0 | 6 |  |  | his, point, writable, sensor | Bool
6 | 6 | Pmp3Prv | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | Off |  | 1 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Bool
7 | 7 | Pmp4Prv | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | Off |  | 1 | Enabled | 0 | 8 |  |  | his, point, writable, sensor | Bool
8 | 8 | Pmp5Prv | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | On |  | 1 | Enabled | 0 | 9 |  |  | his, point, writable, sensor | Bool |  | Pmp6Prv
9 | 9 | OAT | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | 57.9 | °F | 1000 | Enabled | 0 | 11 |  |  | his, point, writable, sensor | Number | fahrenheit | Pmp7Prv
10 | 10 | EmerShutDn | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | Off |  | 1 | Enabled | 0 | 13 |  |  | his, point, writable, sensor | Bool |  | Dom HwPump
11 | 11 | OAH | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | 0.42 |  | 1000 | Enabled | 0 | 12 |  |  | his, point, writable, sensor | Number |  | Perimeter Pump OA Start SP
12 | 12 | BoilerRmTmp | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | 80.37 | °F | 1000 | Enabled | 0 | 15 |  |  | his, point, writable, sensor | Number | fahrenheit | Set point
13 | 13 | Pmp8Prv | Hanson\CX1\Boiler | boiler | 10.1.13.71/pe/boiler.xml | Off |  | 1 | Enabled | 0 | 10 |  |  | his, point, writable, sensor | Bool
14 | 14 | PressBldg | Hanson\CX1\RTU1 | rtu1 | 10.1.13.71/pe/rtu1.xml | 0.08 |  | 1000 | Enabled | 0 | 4 | 10.1.13.71/pe/rtu1.xml | ahu, rtu | his, point, writable, sensor | Number |  | StPt
15 | 15 | RACO2 | Hanson\CX1\RTU1 | rtu1 | 10.1.13.71/pe/rtu1.xml | 601 | ppm | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | parts_per_million | Occupy
16 | 16 | RAH | Hanson\CX1\RTU1 | rtu1 | 10.1.13.71/pe/rtu1.xml | 0.27 | Rh | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number | percent_relative_humidity | Schedule | Decimal place error when pulled into SkySpark. (*100 to correct)
17 | 17 | SFanPrv | Hanson\CX1\RTU1 | rtu1 | 10.1.13.71/pe/rtu1.xml | On |  | 1 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Bool |  | Supply Air Set Point
18 | 18 | EFan2Prv | Hanson\CX1\RTU1 | rtu1 | 10.1.13.71/pe/rtu1.xml | On |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool
19 | 19 | SFanPrv | Hanson\CX1\RTU2 | rtu2 | 10.1.13.71/pe/rtu2.xml | On |  | 1 | Enabled | 0 | 1 | 10.1.13.71/pe/rtu2.xml | ahu, rtu | his, point, writable, sensor | Bool |  | StPt
20 | 20 | RAH | Hanson\CX1\RTU2 | rtu2 | 10.1.13.71/pe/rtu2.xml | 0.39 | Rh | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number | percent_relative_humidity | Occupy | rtu2 is titled unusually when you select it, it doesn't seem to point to a site?
21 | 21 | RACO2 | Hanson\CX1\RTU2 | rtu2 | 10.1.13.71/pe/rtu2.xml | 230.2 | ppm | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | parts_per_million | Schedule
22 | 22 | PressBldg | Hanson\CX1\RTU2 | rtu2 | 10.1.13.71/pe/rtu2.xml | 0 |  | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number |  | Supply Air Set Point
23 | 23 | ExFan1Prv | Hanson\CX1\RTU2 | rtu2 | 10.1.13.71/pe/rtu2.xml | On |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool
24 | 24 | RMT | Hanson\CX1\VAV1.1 | vav1.1 | 10.1.13.71/pe/vav1.1.xml | 73.4 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav1.1.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit | Cool StPt
25 | 25 | RMT_UH4 | Hanson\CX1\VAV1.1 | vav1.1 | 10.1.13.71/pe/vav1.1.xml | 81.2 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit | Heat StPt
26 | 26 | DAT | Hanson\CX1\VAV1.1 | vav1.1 | 10.1.13.71/pe/vav1.1.xml | 72.8 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit | AdjCool
27 | 27 | VP | Hanson\CX1\VAV1.1 | vav1.1 | 10.1.13.71/pe/vav1.1.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number |  | AdjHeat
28 | 28 | AdjStPt | Hanson\CX1\VAV1.1 | vav1.1 | 10.1.13.71/pe/vav1.1.xml | -1.87 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number |  | DAT
29 | 29 | VP | Hanson\CX1\VAV1.10 | vav1.10 | 10.1.13.71/pe/vav1.10.xml | 0.02 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav1.10.xml | airTerminalUnit, vav | his, point, writable, sensor | Number |  | CFM StPt
30 | 30 | DAT | Hanson\CX1\VAV1.10 | vav1.10 | 10.1.13.71/pe/vav1.10.xml | 58.9 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit | Max CFMSp
31 | 31 | RMT | Hanson\CX1\VAV1.10 | vav1.10 | 10.1.13.71/pe/vav1.10.xml | 72.2 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit | MinCFMSp
32 | 32 | AdjStPt | Hanson\CX1\VAV1.10 | vav1.10 | 10.1.13.71/pe/vav1.10.xml | -1.87 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number |  | Damper
33 | 33 | Ovr | Hanson\CX1\VAV1.10 | vav1.10 | 10.1.13.71/pe/vav1.10.xml | Off |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool |  | RHt Vlv
34 | 34 | VP | Hanson\CX1\VAV1.2 | vav1.2 | 10.1.13.71/pe/vav1.2.xml | 0.02 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav1.2.xml | airTerminalUnit, vav | his, point, writable, sensor | Number |  | Area Served
35 | 35 | DAT | Hanson\CX1\VAV1.2 | vav1.2 | 10.1.13.71/pe/vav1.2.xml | 85 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit | Fintube
36 | 36 | RMT | Hanson\CX1\VAV1.2 | vav1.2 | 10.1.13.71/pe/vav1.2.xml | 73.6 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit | RmT B
37 | 37 | AdjStPt | Hanson\CX1\VAV1.2 | vav1.2 | 10.1.13.71/pe/vav1.2.xml | 2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number |  | RmT C
38 | 38 | RMT_A | Hanson\CX1\VAV1.3 | vav1.3 | 10.1.13.71/pe/vav1.3.xml | 72.7 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav1.3.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit | RmT D
39 | 39 | AdjStPt | Hanson\CX1\VAV1.3 | vav1.3 | 10.1.13.71/pe/vav1.3.xml | -1.815 | °F | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number | fahrenheit
40 | 40 | VP | Hanson\CX1\VAV1.3 | vav1.3 | 10.1.13.71/pe/vav1.3.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
41 | 41 | RMT_B | Hanson\CX1\VAV1.3 | vav1.3 | 10.1.13.71/pe/vav1.3.xml | 73.6 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
42 | 42 | RMT_C | Hanson\CX1\VAV1.3 | vav1.3 | 10.1.13.71/pe/vav1.3.xml | 73.4 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
43 | 43 | RMT_D | Hanson\CX1\VAV1.3 | vav1.3 | 10.1.13.71/pe/vav1.3.xml | 74.1 | °F | 1000 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Number | fahrenheit
44 | 44 | DAT | Hanson\CX1\VAV1.3.2 | vav1.3.2 | 10.1.13.71/pe/vav1.3.2.xml | 56.8 |  | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav1.3.2.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
45 | 45 | RMT_A | Hanson\CX1\VAV1.4 | vav1.4 | 10.1.13.71/pe/vav1.4.xml | 77.8 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav1.4.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
46 | 46 | DAT | Hanson\CX1\VAV1.4 | vav1.4 | 10.1.13.71/pe/vav1.4.xml | 57.4 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
47 | 47 | VP | Hanson\CX1\VAV1.4 | vav1.4 | 10.1.13.71/pe/vav1.4.xml | 0.51 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
48 | 48 | RMT_B | Hanson\CX1\VAV1.4 | vav1.4 | 10.1.13.71/pe/vav1.4.xml | 72.7 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
49 | 49 | AdjStPt | Hanson\CX1\VAV1.4 | vav1.4 | 10.1.13.71/pe/vav1.4.xml | 0.11 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
50 | 50 | Ovr | Hanson\CX1\VAV1.4 | vav1.4 | 10.1.13.71/pe/vav1.4.xml | Off |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool
51 | 51 | DAT | Hanson\CX1\VAV1.5 | vav1.5 | 10.1.13.71/pe/vav1.5.xml | 58.4 | °F | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav1.5.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
52 | 52 | RMT | Hanson\CX1\VAV1.5 | vav1.5 | 10.1.13.71/pe/vav1.5.xml | 73.1 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
53 | 53 | VP | Hanson\CX1\VAV1.5 | vav1.5 | 10.1.13.71/pe/vav1.5.xml | 0.2 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
54 | 54 | RMT_C | Hanson\CX1\VAV1.6 | vav1.6 | 10.1.13.71/pe/vav1.6.xml | 72.6 | °F | 1000 | Enabled | 0 | 5 | 10.1.13.71/pe/vav1.6.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
55 | 55 | RMT_UH5 | Hanson\CX1\VAV1.6 | vav1.6 | 10.1.13.71/pe/vav1.6.xml | 73.7 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
56 | 56 | RMT_B | Hanson\CX1\VAV1.6 | vav1.6 | 10.1.13.71/pe/vav1.6.xml | 70.8 | °F | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number | fahrenheit
57 | 57 | VP | Hanson\CX1\VAV1.6 | vav1.6 | 10.1.13.71/pe/vav1.6.xml | 0.04 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
58 | 58 | DAT | Hanson\CX1\VAV1.6 | vav1.6 | 10.1.13.71/pe/vav1.6.xml | 58.9 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
59 | 59 | RMT_A | Hanson\CX1\VAV1.6 | vav1.6 | 10.1.13.71/pe/vav1.6.xml | 75 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
60 | 60 | VP | Hanson\CX1\VAV1.7 | vav1.7 | 10.1.13.71/pe/vav1.7.xml | 0.01 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav1.7.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
61 | 61 | DAT | Hanson\CX1\VAV1.7 | vav1.7 | 10.1.13.71/pe/vav1.7.xml | 58.8 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
62 | 62 | RMT | Hanson\CX1\VAV1.7 | vav1.7 | 10.1.13.71/pe/vav1.7.xml | 71.9 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
63 | 63 | AdjStPt | Hanson\CX1\VAV1.7 | vav1.7 | 10.1.13.71/pe/vav1.7.xml | 0.91 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
64 | 64 | VP | Hanson\CX1\VAV1.8 | vav1.8 | 10.1.13.71/pe/vav1.8.xml | 0.02 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav1.8.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
65 | 65 | DAT | Hanson\CX1\VAV1.8 | vav1.8 | 10.1.13.71/pe/vav1.8.xml | 86.1 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
66 | 66 | RMT | Hanson\CX1\VAV1.8 | vav1.8 | 10.1.13.71/pe/vav1.8.xml | 73.9 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
67 | 67 | AdjStPt | Hanson\CX1\VAV1.8 | vav1.8 | 10.1.13.71/pe/vav1.8.xml | 2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
68 | 68 | VP | Hanson\CX1\VAV1.9 | vav1.9 | 10.1.13.71/pe/vav1.9.xml | 0.16 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav1.9.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
69 | 69 | DAT | Hanson\CX1\VAV1.9 | vav1.9 | 10.1.13.71/pe/vav1.9.xml | 57.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
70 | 70 | RMT_UH2 | Hanson\CX1\VAV1.9 | vav1.9 | 10.1.13.71/pe/vav1.9.xml | 73.7 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
71 | 71 | RMT | Hanson\CX1\VAV1.9 | vav1.9 | 10.1.13.71/pe/vav1.9.xml | 73.2 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
72 | 72 | AdjStPt | Hanson\CX1\VAV1.9 | vav1.9 | 10.1.13.71/pe/vav1.9.xml | 0.86 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
73 | 73 | VP | Hanson\CX1\VAV2.1 | vav2.1 | 10.1.13.71/pe/vav2.1.xml | 0.14 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav2.1.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
74 | 74 | DAT | Hanson\CX1\VAV2.1 | vav2.1 | 10.1.13.71/pe/vav2.1.xml | 70.8 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
75 | 75 | RMT_B | Hanson\CX1\VAV2.1 | vav2.1 | 10.1.13.71/pe/vav2.1.xml | 71.3 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
76 | 76 | RMT_A | Hanson\CX1\VAV2.1 | vav2.1 | 10.1.13.71/pe/vav2.1.xml | 72.6 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
77 | 77 | RMT_C | Hanson\CX1\VAV2.1 | vav2.1 | 10.1.13.71/pe/vav2.1.xml | 73.1 | °F | 1000 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Number | fahrenheit
78 | 78 | AdjStPt | Hanson\CX1\VAV2.1 | vav2.1 | 10.1.13.71/pe/vav2.1.xml | 2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
79 | 79 | RMT_A | Hanson\CX1\VAV2.10 | vav2.10 | 10.1.13.71/pe/vav2.10.xml | 72.2 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav2.10.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
80 | 80 | RMT_B | Hanson\CX1\VAV2.10 | vav2.10 | 10.1.13.71/pe/vav2.10.xml | 72.6 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
81 | 81 | DAT | Hanson\CX1\VAV2.10 | vav2.10 | 10.1.13.71/pe/vav2.10.xml | 72.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
82 | 82 | VP | Hanson\CX1\VAV2.10 | vav2.10 | 10.1.13.71/pe/vav2.10.xml | 0.08 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
83 | 83 | AdjStPt | Hanson\CX1\VAV2.10 | vav2.10 | 10.1.13.71/pe/vav2.10.xml | -0.77 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
84 | 84 | VP | Hanson\CX1\VAV2.11 | vav2.11 | 10.1.13.71/pe/vav2.11.xml | 0.1 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav2.11.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
85 | 85 | DAT | Hanson\CX1\VAV2.11 | vav2.11 | 10.1.13.71/pe/vav2.11.xml | 56.7 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
86 | 86 | RMT_B | Hanson\CX1\VAV2.11 | vav2.11 | 10.1.13.71/pe/vav2.11.xml | 72.9 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
87 | 87 | RMT_A | Hanson\CX1\VAV2.11 | vav2.11 | 10.1.13.71/pe/vav2.11.xml | 71 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
88 | 88 | AdjStPt | Hanson\CX1\VAV2.11 | vav2.11 | 10.1.13.71/pe/vav2.11.xml | -2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
89 | 89 | RMT_A | Hanson\CX1\VAV2.12 | vav2.12 | 10.1.13.71/pe/vav2.12.xml | 73.6 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav2.12.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
90 | 90 | DAT | Hanson\CX1\VAV2.12 | vav2.12 | 10.1.13.71/pe/vav2.12.xml | 56.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
91 | 91 | VP | Hanson\CX1\VAV2.12 | vav2.12 | 10.1.13.71/pe/vav2.12.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
92 | 92 | RMT_B | Hanson\CX1\VAV2.12 | vav2.12 | 10.1.13.71/pe/vav2.12.xml | 72.4 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
93 | 93 | AdjStPt | Hanson\CX1\VAV2.12 | vav2.12 | 10.1.13.71/pe/vav2.12.xml | 0.39 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
94 | 94 | RMT_A | Hanson\CX1\VAV2.13 | vav2.13 | 10.1.13.71/pe/vav2.13.xml | 74.5 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav2.13.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
95 | 95 | DAT | Hanson\CX1\VAV2.13 | vav2.13 | 10.1.13.71/pe/vav2.13.xml | 76.8 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
96 | 96 | VP | Hanson\CX1\VAV2.13 | vav2.13 | 10.1.13.71/pe/vav2.13.xml | 0.05 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
97 | 97 | RMT_B | Hanson\CX1\VAV2.13 | vav2.13 | 10.1.13.71/pe/vav2.13.xml | 73.4 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
98 | 98 | AdjStPt | Hanson\CX1\VAV2.13 | vav2.13 | 10.1.13.71/pe/vav2.13.xml | 1.22 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
99 | 99 | DAT | Hanson\CX1\VAV2.14 | vav2.14 | 10.1.13.71/pe/vav2.14.xml | 58.8 | °F | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav2.14.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
100 | 100 | RMT | Hanson\CX1\VAV2.14 | vav2.14 | 10.1.13.71/pe/vav2.14.xml | 74.1 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
101 | 101 | VP | Hanson\CX1\VAV2.14 | vav2.14 | 10.1.13.71/pe/vav2.14.xml | 0.25 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
102 | 102 | DAT | Hanson\CX1\VAV2.15 | vav2.15 | 10.1.13.71/pe/vav2.15.xml | 63.6 | °F | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav2.15.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
103 | 103 | RMT | Hanson\CX1\VAV2.15 | vav2.15 | 10.1.13.71/pe/vav2.15.xml | 71.5 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
104 | 104 | VP | Hanson\CX1\VAV2.15 | vav2.15 | 10.1.13.71/pe/vav2.15.xml | 0.07 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
105 | 105 | RMT_A | Hanson\CX1\VAV2.16 | vav2.16 | 10.1.13.71/pe/vav2.16.xml | 73.4 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav2.16.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
106 | 106 | DAT | Hanson\CX1\VAV2.16 | vav2.16 | 10.1.13.71/pe/vav2.16.xml | 56.3 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
107 | 107 | VP | Hanson\CX1\VAV2.16 | vav2.16 | 10.1.13.71/pe/vav2.16.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
108 | 108 | RMT_B | Hanson\CX1\VAV2.16 | vav2.16 | 10.1.13.71/pe/vav2.16.xml | 73.4 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
109 | 109 | AdjStPt | Hanson\CX1\VAV2.16 | vav2.16 | 10.1.13.71/pe/vav2.16.xml | 1.37 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
110 | 110 | RMT_B | Hanson\CX1\VAV2.2 | vav2.2 | 10.1.13.71/pe/vav2.2.xml | 71.9 | °F | 1000 | Enabled | 0 | 3 | 10.1.13.71/pe/vav2.2.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
111 | 111 | VP | Hanson\CX1\VAV2.2 | vav2.2 | 10.1.13.71/pe/vav2.2.xml | 0.04 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
112 | 112 | DAT | Hanson\CX1\VAV2.2 | vav2.2 | 10.1.13.71/pe/vav2.2.xml | 59.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
113 | 113 | RMT_A | Hanson\CX1\VAV2.2 | vav2.2 | 10.1.13.71/pe/vav2.2.xml | 72.4 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
114 | 114 | AdjStPt | Hanson\CX1\VAV2.2 | vav2.2 | 10.1.13.71/pe/vav2.2.xml | -1.89 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
115 | 115 | RMT_A | Hanson\CX1\VAV2.3 | vav2.3 | 10.1.13.71/pe/vav2.3.xml | 73.2 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav2.3.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
116 | 116 | DAT | Hanson\CX1\VAV2.3 | vav2.3 | 10.1.13.71/pe/vav2.3.xml | 58.2 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
117 | 117 | VP | Hanson\CX1\VAV2.3 | vav2.3 | 10.1.13.71/pe/vav2.3.xml | 0.16 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
118 | 118 | RMT_B | Hanson\CX1\VAV2.3 | vav2.3 | 10.1.13.71/pe/vav2.3.xml | 73.8 | °F | 1000 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Number | fahrenheit
119 | 119 | RMT_UH3 | Hanson\CX1\VAV2.3 | vav2.3 | 10.1.13.71/pe/vav2.3.xml | 74.1 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
120 | 120 | AdjStPt | Hanson\CX1\VAV2.3 | vav2.3 | 10.1.13.71/pe/vav2.3.xml | 1.89 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
121 | 121 | VP | Hanson\CX1\VAV2.4 | vav2.4 | 10.1.13.71/pe/vav2.4.xml | 0.01 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav2.4.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
122 | 122 | RMT | Hanson\CX1\VAV2.4 | vav2.4 | 10.1.13.71/pe/vav2.4.xml | 73.6 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
123 | 123 | DAT | Hanson\CX1\VAV2.4 | vav2.4 | 10.1.13.71/pe/vav2.4.xml | 61 | °F | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number | fahrenheit
124 | 124 | RMT_A | Hanson\CX1\VAV2.5 | vav2.5 | 10.1.13.71/pe/vav2.5.xml | 73.2 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav2.5.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
125 | 125 | DAT | Hanson\CX1\VAV2.5 | vav2.5 | 10.1.13.71/pe/vav2.5.xml | 56.7 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
126 | 126 | VP | Hanson\CX1\VAV2.5 | vav2.5 | 10.1.13.71/pe/vav2.5.xml | 0.1 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
127 | 127 | RMT_B | Hanson\CX1\VAV2.5 | vav2.5 | 10.1.13.71/pe/vav2.5.xml | 72.2 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
128 | 128 | AdjStPt | Hanson\CX1\VAV2.5 | vav2.5 | 10.1.13.71/pe/vav2.5.xml | -1.47 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
129 | 129 | Ovr | Hanson\CX1\VAV2.5 | vav2.5 | 10.1.13.71/pe/vav2.5.xml | Off |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool
130 | 130 | RMT_B | Hanson\CX1\VAV2.6 | vav2.6 | 10.1.13.71/pe/vav2.6.xml | 73.2 | °F | 1000 | Enabled | 0 | 3 | 10.1.13.71/pe/vav2.6.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
131 | 131 | VP | Hanson\CX1\VAV2.6 | vav2.6 | 10.1.13.71/pe/vav2.6.xml | 0.09 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
132 | 132 | DAT | Hanson\CX1\VAV2.6 | vav2.6 | 10.1.13.71/pe/vav2.6.xml | 56.3 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
133 | 133 | RMT_A | Hanson\CX1\VAV2.6 | vav2.6 | 10.1.13.71/pe/vav2.6.xml | 71.9 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
134 | 134 | Ovr | Hanson\CX1\VAV2.6 | vav2.6 | 10.1.13.71/pe/vav2.6.xml | Off |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool
135 | 135 | VP | Hanson\CX1\VAV2.7 | vav2.7 | 10.1.13.71/pe/vav2.7.xml | 0.32 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav2.7.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
136 | 136 | DAT | Hanson\CX1\VAV2.7 | vav2.7 | 10.1.13.71/pe/vav2.7.xml | 58.93 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
137 | 137 | RMT_A | Hanson\CX1\VAV2.7 | vav2.7 | 10.1.13.71/pe/vav2.7.xml | 73.2 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
138 | 138 | RMT_B | Hanson\CX1\VAV2.7 | vav2.7 | 10.1.13.71/pe/vav2.7.xml | 71.9 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
139 | 139 | RMT_C | Hanson\CX1\VAV2.7 | vav2.7 | 10.1.13.71/pe/vav2.7.xml | 72.6 | °F | 1000 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Number | fahrenheit
140 | 140 | AdjStPt | Hanson\CX1\VAV2.7 | vav2.7 | 10.1.13.71/pe/vav2.7.xml | 0.1 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
141 | 141 | VP | Hanson\CX1\VAV2.8 | vav2.8 | 10.1.13.71/pe/vav2.8.xml | 0.04 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav2.8.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
142 | 142 | DAT | Hanson\CX1\VAV2.8 | vav2.8 | 10.1.13.71/pe/vav2.8.xml | 73 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
143 | 143 | RMT | Hanson\CX1\VAV2.8 | vav2.8 | 10.1.13.71/pe/vav2.8.xml | 72.6 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
144 | 144 | AdjStPt | Hanson\CX1\VAV2.8 | vav2.8 | 10.1.13.71/pe/vav2.8.xml | -2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
145 | 145 | RMT_A | Hanson\CX1\VAV2.9 | vav2.9 | 10.1.13.71/pe/vav2.9.xml | 72 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav2.9.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
146 | 146 | DAT | Hanson\CX1\VAV2.9 | vav2.9 | 10.1.13.71/pe/vav2.9.xml | 58.1 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
147 | 147 | VP | Hanson\CX1\VAV2.9 | vav2.9 | 10.1.13.71/pe/vav2.9.xml | 0.3 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
148 | 148 | RMT_B | Hanson\CX1\VAV2.9 | vav2.9 | 10.1.13.71/pe/vav2.9.xml | 71.9 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
149 | 149 | AdjStPt | Hanson\CX1\VAV2.9 | vav2.9 | 10.1.13.71/pe/vav2.9.xml | -1.91 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
150 | 150 | RMT_A | Hanson\CX1\VAV3.1 | vav3.1 | 10.1.13.71/pe/vav3.1.xml | 72.9 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav3.1.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
151 | 151 | DAT | Hanson\CX1\VAV3.1 | vav3.1 | 10.1.13.71/pe/vav3.1.xml | 58.1 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
152 | 152 | VP | Hanson\CX1\VAV3.1 | vav3.1 | 10.1.13.71/pe/vav3.1.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
153 | 153 | RMT_B | Hanson\CX1\VAV3.1 | vav3.1 | 10.1.13.71/pe/vav3.1.xml | 72.7 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
154 | 154 | AdjStPt | Hanson\CX1\VAV3.1 | vav3.1 | 10.1.13.71/pe/vav3.1.xml | 2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
155 | 155 | RMT_A | Hanson\CX1\VAV3.10 | vav3.10 | 10.1.13.71/pe/vav3.10.xml | 73.1 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav3.10.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
156 | 156 | DAT | Hanson\CX1\VAV3.10 | vav3.10 | 10.1.13.71/pe/vav3.10.xml | 81.2 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
157 | 157 | VP | Hanson\CX1\VAV3.10 | vav3.10 | 10.1.13.71/pe/vav3.10.xml | 0.06 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
158 | 158 | RMT_B | Hanson\CX1\VAV3.10 | vav3.10 | 10.1.13.71/pe/vav3.10.xml | 73.9 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
159 | 159 | AdjStPt | Hanson\CX1\VAV3.10 | vav3.10 | 10.1.13.71/pe/vav3.10.xml | 2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
160 | 160 | RMT_A | Hanson\CX1\VAV3.11 | vav3.11 | 10.1.13.71/pe/vav3.11.xml | 74.1 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav3.11.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
161 | 161 | DAT | Hanson\CX1\VAV3.11 | vav3.11 | 10.1.13.71/pe/vav3.11.xml | 67 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
162 | 162 | VP | Hanson\CX1\VAV3.11 | vav3.11 | 10.1.13.71/pe/vav3.11.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
163 | 163 | RMT_B | Hanson\CX1\VAV3.11 | vav3.11 | 10.1.13.71/pe/vav3.11.xml | 73.1 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
164 | 164 | AdjStPt | Hanson\CX1\VAV3.11 | vav3.11 | 10.1.13.71/pe/vav3.11.xml | -0.72 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
165 | 165 | AdjStPt | Hanson\CX1\VAV3.12 | vav3.12 | 10.1.13.71/pe/vav3.12.xml | 2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav3.12.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
166 | 166 | RMT_A | Hanson\CX1\VAV3.12 | vav3.12 | 10.1.13.71/pe/vav3.12.xml | 73.1 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
167 | 167 | RMT_B | Hanson\CX1\VAV3.12 | vav3.12 | 10.1.13.71/pe/vav3.12.xml | 73.2 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
168 | 168 | DAT | Hanson\CX1\VAV3.12 | vav3.12 | 10.1.13.71/pe/vav3.12.xml | 59.1 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
169 | 169 | VP | Hanson\CX1\VAV3.12 | vav3.12 | 10.1.13.71/pe/vav3.12.xml | 0.05 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
170 | 170 | DAT | Hanson\CX1\VAV3.13 | vav3.13 | 10.1.13.71/pe/vav3.13.xml | 58.9 | °F | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav3.13.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
171 | 171 | RMT | Hanson\CX1\VAV3.13 | vav3.13 | 10.1.13.71/pe/vav3.13.xml | 72.9 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
172 | 172 | VP | Hanson\CX1\VAV3.13 | vav3.13 | 10.1.13.71/pe/vav3.13.xml | 0.02 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
173 | 173 | AdjStPt | Hanson\CX1\VAV3.13 | vav3.13 | 10.1.13.71/pe/vav3.13.xml | -1.9 |  | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number
174 | 174 | RMT_A | Hanson\CX1\VAV3.2 | vav3.2 | 10.1.13.71/pe/vav3.2.xml | 72.7 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav3.2.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
175 | 175 | DAT | Hanson\CX1\VAV3.2 | vav3.2 | 10.1.13.71/pe/vav3.2.xml | 59.1 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
176 | 176 | VP | Hanson\CX1\VAV3.2 | vav3.2 | 10.1.13.71/pe/vav3.2.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
177 | 177 | RMT_B | Hanson\CX1\VAV3.2 | vav3.2 | 10.1.13.71/pe/vav3.2.xml | 71.9 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
178 | 178 | AdjStPt | Hanson\CX1\VAV3.2 | vav3.2 | 10.1.13.71/pe/vav3.2.xml | 1.24 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
179 | 179 | RMT_B | Hanson\CX1\VAV3.3 | vav3.3 | 10.1.13.71/pe/vav3.3.xml | 72.4 | °F | 1000 | Enabled | 0 | 3 | 10.1.13.71/pe/vav3.3.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
180 | 180 | RMT_A | Hanson\CX1\VAV3.3 | vav3.3 | 10.1.13.71/pe/vav3.3.xml | 72.9 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
181 | 181 | DAT | Hanson\CX1\VAV3.3 | vav3.3 | 10.1.13.71/pe/vav3.3.xml | 58.1 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
182 | 182 | VP | Hanson\CX1\VAV3.3 | vav3.3 | 10.1.13.71/pe/vav3.3.xml | 0.16 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
183 | 183 | AdjStPt | Hanson\CX1\VAV3.3 | vav3.3 | 10.1.13.71/pe/vav3.3.xml | 2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
184 | 184 | Ovr | Hanson\CX1\VAV3.3 | vav3.3 | 10.1.13.71/pe/vav3.3.xml | Off |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool
185 | 185 | DAT | Hanson\CX1\VAV3.4 | vav3.4 | 10.1.13.71/pe/vav3.4.xml | 73.5 | °F | 1000 | Enabled | 0 | 4 | 10.1.13.71/pe/vav3.4.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
186 | 186 | RMT | Hanson\CX1\VAV3.4 | vav3.4 | 10.1.13.71/pe/vav3.4.xml | 72 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
187 | 187 | VP | Hanson\CX1\VAV3.4 | vav3.4 | 10.1.13.71/pe/vav3.4.xml | 0 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
188 | 188 | AdjStPt | Hanson\CX1\VAV3.4 | vav3.4 | 10.1.13.71/pe/vav3.4.xml | 2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
189 | 189 | RMT_A | Hanson\CX1\VAV3.5 | vav3.5 | 10.1.13.71/pe/vav3.5.xml | 73.4 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav3.5.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
190 | 190 | DAT | Hanson\CX1\VAV3.5 | vav3.5 | 10.1.13.71/pe/vav3.5.xml | 56.7 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
191 | 191 | VP | Hanson\CX1\VAV3.5 | vav3.5 | 10.1.13.71/pe/vav3.5.xml | 0.07 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
192 | 192 | RMT_B | Hanson\CX1\VAV3.5 | vav3.5 | 10.1.13.71/pe/vav3.5.xml | 72.9 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
193 | 193 | RMT_C | Hanson\CX1\VAV3.5 | vav3.5 | 10.1.13.71/pe/vav3.5.xml | 73.9 | °F | 1000 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Number | fahrenheit
194 | 194 | AdjStPt | Hanson\CX1\VAV3.5 | vav3.5 | 10.1.13.71/pe/vav3.5.xml | 0.6 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
195 | 195 | VP | Hanson\CX1\VAV3.6 | vav3.6 | 10.1.13.71/pe/vav3.6.xml | 0.08 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav3.6.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
196 | 196 | DAT | Hanson\CX1\VAV3.6 | vav3.6 | 10.1.13.71/pe/vav3.6.xml | 56.7 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
197 | 197 | RMT_A | Hanson\CX1\VAV3.6 | vav3.6 | 10.1.13.71/pe/vav3.6.xml | 73.1 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
198 | 198 | RMT_B | Hanson\CX1\VAV3.6 | vav3.6 | 10.1.13.71/pe/vav3.6.xml | 72.7 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
199 | 199 | RMT_C | Hanson\CX1\VAV3.6 | vav3.6 | 10.1.13.71/pe/vav3.6.xml | 73.1 | °F | 1000 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Number | fahrenheit
200 | 200 | AdjStPt | Hanson\CX1\VAV3.6 | vav3.6 | 10.1.13.71/pe/vav3.6.xml | -1.76 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
201 | 201 | RMT_C | Hanson\CX1\VAV3.7 | vav3.7 | 10.1.13.71/pe/vav3.7.xml | 72.9 | °F | 1000 | Enabled | 0 | 5 | 10.1.13.71/pe/vav3.7.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
202 | 202 | RMT_B | Hanson\CX1\VAV3.7 | vav3.7 | 10.1.13.71/pe/vav3.7.xml | 73.1 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
203 | 203 | VP | Hanson\CX1\VAV3.7 | vav3.7 | 10.1.13.71/pe/vav3.7.xml | 0.09 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
204 | 204 | DAT | Hanson\CX1\VAV3.7 | vav3.7 | 10.1.13.71/pe/vav3.7.xml | 74.6 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
205 | 205 | RMT_A | Hanson\CX1\VAV3.7 | vav3.7 | 10.1.13.71/pe/vav3.7.xml | 73.4 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
206 | 206 | AdjStPt | Hanson\CX1\VAV3.7 | vav3.7 | 10.1.13.71/pe/vav3.7.xml | 2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
207 | 207 | RMT_A | Hanson\CX1\VAV3.8 | vav3.8 | 10.1.13.71/pe/vav3.8.xml | 72.6 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav3.8.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
208 | 208 | DAT | Hanson\CX1\VAV3.8 | vav3.8 | 10.1.13.71/pe/vav3.8.xml | 56.9 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
209 | 209 | VP | Hanson\CX1\VAV3.8 | vav3.8 | 10.1.13.71/pe/vav3.8.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
210 | 210 | RMT_B | Hanson\CX1\VAV3.8 | vav3.8 | 10.1.13.71/pe/vav3.8.xml | 73.1 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
211 | 211 | AdjStPt | Hanson\CX1\VAV3.8 | vav3.8 | 10.1.13.71/pe/vav3.8.xml | -1.76 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
212 | 212 | Ovr | Hanson\CX1\VAV3.8 | vav3.8 | 10.1.13.71/pe/vav3.8.xml | Off |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool
213 | 213 | RMT_B | Hanson\CX1\VAV3.9 | vav3.9 | 10.1.13.71/pe/vav3.9.xml | 72.2 | °F | 1000 | Enabled | 0 | 3 | 10.1.13.71/pe/vav3.9.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
214 | 214 | RMT_A | Hanson\CX1\VAV3.9 | vav3.9 | 10.1.13.71/pe/vav3.9.xml | 71.5 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
215 | 215 | DAT | Hanson\CX1\VAV3.9 | vav3.9 | 10.1.13.71/pe/vav3.9.xml | 56.7 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
216 | 216 | VP | Hanson\CX1\VAV3.9 | vav3.9 | 10.1.13.71/pe/vav3.9.xml | 0.09 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
217 | 217 | AdjStPt | Hanson\CX1\VAV3.9 | vav3.9 | 10.1.13.71/pe/vav3.9.xml | -2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
218 | 218 | VP | Hanson\CX1\VAV4.1 | vav4.1 | 10.1.13.71/pe/vav4.1.xml | 0.05 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav4.1.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
219 | 219 | DAT | Hanson\CX1\VAV4.1 | vav4.1 | 10.1.13.71/pe/vav4.1.xml | 56.7 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
220 | 220 | RMT_A | Hanson\CX1\VAV4.1 | vav4.1 | 10.1.13.71/pe/vav4.1.xml | 73.2 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
221 | 221 | RMT_B | Hanson\CX1\VAV4.1 | vav4.1 | 10.1.13.71/pe/vav4.1.xml | 73.1 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
222 | 222 | AdjStPt | Hanson\CX1\VAV4.1 | vav4.1 | 10.1.13.71/pe/vav4.1.xml | 0.9 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
223 | 223 | AdjStPt | Hanson\CX1\VAV4.10 | vav4.10 | 10.1.13.71/pe/vav4.10.xml | -1.74 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav4.10.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
224 | 224 | RMT_B | Hanson\CX1\VAV4.10 | vav4.10 | 10.1.13.71/pe/vav4.10.xml | 71 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
225 | 225 | RMT_A | Hanson\CX1\VAV4.10 | vav4.10 | 10.1.13.71/pe/vav4.10.xml | 71.2 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
226 | 226 | DAT | Hanson\CX1\VAV4.10 | vav4.10 | 10.1.13.71/pe/vav4.10.xml | 57.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
227 | 227 | VP | Hanson\CX1\VAV4.10 | vav4.10 | 10.1.13.71/pe/vav4.10.xml | 0.05 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
228 | 228 | RMT_A | Hanson\CX1\VAV4.11 | vav4.11 | 10.1.13.71/pe/vav4.11.xml | 72.4 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav4.11.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
229 | 229 | DAT | Hanson\CX1\VAV4.11 | vav4.11 | 10.1.13.71/pe/vav4.11.xml | 65.8 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
230 | 230 | VP | Hanson\CX1\VAV4.11 | vav4.11 | 10.1.13.71/pe/vav4.11.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
231 | 231 | RMT_B | Hanson\CX1\VAV4.11 | vav4.11 | 10.1.13.71/pe/vav4.11.xml | 72.6 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
232 | 232 | AdjStPt | Hanson\CX1\VAV4.11 | vav4.11 | 10.1.13.71/pe/vav4.11.xml | 1.91 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
233 | 233 | RMT_A | Hanson\CX1\VAV4.12 | vav4.12 | 10.1.13.71/pe/vav4.12.xml | 73.9 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav4.12.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
234 | 234 | DAT | Hanson\CX1\VAV4.12 | vav4.12 | 10.1.13.71/pe/vav4.12.xml | 81.2 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
235 | 235 | VP | Hanson\CX1\VAV4.12 | vav4.12 | 10.1.13.71/pe/vav4.12.xml | 0.02 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
236 | 236 | RMT_B | Hanson\CX1\VAV4.12 | vav4.12 | 10.1.13.71/pe/vav4.12.xml | 73.9 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
237 | 237 | AdjStPt | Hanson\CX1\VAV4.12 | vav4.12 | 10.1.13.71/pe/vav4.12.xml | 2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
238 | 238 | RMT_A | Hanson\CX1\VAV4.2 | vav4.2 | 10.1.13.71/pe/vav4.2.xml | 70.7 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav4.2.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
239 | 239 | DAT | Hanson\CX1\VAV4.2 | vav4.2 | 10.1.13.71/pe/vav4.2.xml | 56.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
240 | 240 | VP | Hanson\CX1\VAV4.2 | vav4.2 | 10.1.13.71/pe/vav4.2.xml | 0.66 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
241 | 241 | RMT_B | Hanson\CX1\VAV4.2 | vav4.2 | 10.1.13.71/pe/vav4.2.xml | 72.9 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
242 | 242 | AdjStPt | Hanson\CX1\VAV4.2 | vav4.2 | 10.1.13.71/pe/vav4.2.xml | -2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
243 | 243 | VP | Hanson\CX1\VAV4.3 | vav4.3 | 10.1.13.71/pe/vav4.3.xml | 0.05 |  | 1000 | Enabled | 0 | 7 | 10.1.13.71/pe/vav4.3.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
244 | 244 | DAT | Hanson\CX1\VAV4.3 | vav4.3 | 10.1.13.71/pe/vav4.3.xml | 57.9 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
245 | 245 | RMT | Hanson\CX1\VAV4.3 | vav4.3 | 10.1.13.71/pe/vav4.3.xml | 72.7 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
246 | 246 | Ovr | Hanson\CX1\VAV4.3 | vav4.3 | 10.1.13.71/pe/vav4.3.xml | Off |  | 1 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Bool
247 | 247 | DAT | Hanson\CX1\VAV4.4 | vav4.4 | 10.1.13.71/pe/vav4.4.xml | 58.2 | °F | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav4.4.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
248 | 248 | RMT | Hanson\CX1\VAV4.4 | vav4.4 | 10.1.13.71/pe/vav4.4.xml | 73.1 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
249 | 249 | VP | Hanson\CX1\VAV4.4 | vav4.4 | 10.1.13.71/pe/vav4.4.xml | 0.01 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
250 | 250 | RMT_C | Hanson\CX1\VAV4.5 | vav4.5 | 10.1.13.71/pe/vav4.5.xml | 73.1 | °F | 1000 | Enabled | 0 | 5 | 10.1.13.71/pe/vav4.5.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
251 | 251 | RMT_B | Hanson\CX1\VAV4.5 | vav4.5 | 10.1.13.71/pe/vav4.5.xml | 72 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
252 | 252 | VP | Hanson\CX1\VAV4.5 | vav4.5 | 10.1.13.71/pe/vav4.5.xml | 0 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
253 | 253 | DAT | Hanson\CX1\VAV4.5 | vav4.5 | 10.1.13.71/pe/vav4.5.xml | 56.3 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
254 | 254 | RMT_A | Hanson\CX1\VAV4.5 | vav4.5 | 10.1.13.71/pe/vav4.5.xml | 72.9 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
255 | 255 | AdjStPt | Hanson\CX1\VAV4.5 | vav4.5 | 10.1.13.71/pe/vav4.5.xml | -1.92 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
256 | 256 | RMT_A | Hanson\CX1\VAV4.6 | vav4.6 | 10.1.13.71/pe/vav4.6.xml | 73.1 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav4.6.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
257 | 257 | RMT_B | Hanson\CX1\VAV4.6 | vav4.6 | 10.1.13.71/pe/vav4.6.xml | 71.2 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
258 | 258 | RMT_C | Hanson\CX1\VAV4.6 | vav4.6 | 10.1.13.71/pe/vav4.6.xml | 73.9 | °F | 1000 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Number | fahrenheit
259 | 259 | DAT | Hanson\CX1\VAV4.6 | vav4.6 | 10.1.13.71/pe/vav4.6.xml | 56.3 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
260 | 260 | VP | Hanson\CX1\VAV4.6 | vav4.6 | 10.1.13.71/pe/vav4.6.xml | 0.49 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
261 | 261 | AdjStPt | Hanson\CX1\VAV4.6 | vav4.6 | 10.1.13.71/pe/vav4.6.xml | -0.16 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
262 | 262 | RMT_C | Hanson\CX1\VAV4.7 | vav4.7 | 10.1.13.71/pe/vav4.7.xml | 70.5 | °F | 1000 | Enabled | 0 | 5 | 10.1.13.71/pe/vav4.7.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
263 | 263 | RMT_B | Hanson\CX1\VAV4.7 | vav4.7 | 10.1.13.71/pe/vav4.7.xml | 70 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
264 | 264 | VP | Hanson\CX1\VAV4.7 | vav4.7 | 10.1.13.71/pe/vav4.7.xml | 0.09 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
265 | 265 | DAT | Hanson\CX1\VAV4.7 | vav4.7 | 10.1.13.71/pe/vav4.7.xml | 57.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
266 | 266 | RMT_A | Hanson\CX1\VAV4.7 | vav4.7 | 10.1.13.71/pe/vav4.7.xml | 72.9 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
267 | 267 | AdjStPt | Hanson\CX1\VAV4.7 | vav4.7 | 10.1.13.71/pe/vav4.7.xml | -2 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
268 | 268 | RMT_A | Hanson\CX1\VAV4.8 | vav4.8 | 10.1.13.71/pe/vav4.8.xml | 73.2 | °F | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav4.8.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
269 | 269 | DAT | Hanson\CX1\VAV4.8 | vav4.8 | 10.1.13.71/pe/vav4.8.xml | 56.3 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
270 | 270 | VP | Hanson\CX1\VAV4.8 | vav4.8 | 10.1.13.71/pe/vav4.8.xml | 0.14 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
271 | 271 | RMT_B | Hanson\CX1\VAV4.8 | vav4.8 | 10.1.13.71/pe/vav4.8.xml | 71 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
272 | 272 | AdjStPt | Hanson\CX1\VAV4.8 | vav4.8 | 10.1.13.71/pe/vav4.8.xml | -1.73 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
273 | 273 | Ovr | Hanson\CX1\VAV4.8 | vav4.8 | 10.1.13.71/pe/vav4.8.xml | Off |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool
274 | 274 | RMT_B | Hanson\CX1\VAV4.9 | vav4.9 | 10.1.13.71/pe/vav4.9.xml | 71.7 | °F | 1000 | Enabled | 0 | 3 | 10.1.13.71/pe/vav4.9.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
275 | 275 | RMT_A | Hanson\CX1\VAV4.9 | vav4.9 | 10.1.13.71/pe/vav4.9.xml | 72.6 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
276 | 276 | DAT | Hanson\CX1\VAV4.9 | vav4.9 | 10.1.13.71/pe/vav4.9.xml | 56.3 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
277 | 277 | VP | Hanson\CX1\VAV4.9 | vav4.9 | 10.1.13.71/pe/vav4.9.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
278 | 278 | AdjStPt | Hanson\CX1\VAV4.9 | vav4.9 | 10.1.13.71/pe/vav4.9.xml | -1.88 |  | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number
279 | 279 | Pmp6Prv | Hanson\CX2\Pumps | pumps | 10.1.13.71/pe/pumps.xml | Off |  | 1 | Enabled | 0 | 1 | 10.1.13.71/pe/pumps.xml | pump, motor | his, point, writable, sensor | Bool
280 | 280 | Pmp7Prv | Hanson\CX2\Pumps | pumps | 10.1.13.71/pe/pumps.xml | On |  | 1 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Bool
281 | 281 | FreezeStat | Hanson\CX2\RTU1S | rtu1s | 10.1.13.71/pe/rtu1s.xml | Off |  | 1 | Enabled | 0 | 2 | 10.1.13.71/pe/rtu1s.xml | ahu, rtu | his, point, writable, sensor | Bool |  | Supply Air Temperature Setpoint
282 | 282 | PhaseProtection | Hanson\CX2\RTU1S | rtu1s | 10.1.13.71/pe/rtu1s.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool |  | Today's Start Time
283 | 283 | SFanPrv | Hanson\CX2\RTU1S | rtu1s | 10.1.13.71/pe/rtu1s.xml | On |  | 1 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Bool |  | Scheduled Start Time
284 | 284 | SFanVFDTrouble | Hanson\CX2\RTU1S | rtu1s | 10.1.13.71/pe/rtu1s.xml | Off |  | 1 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Bool |  | Scheduled Stop Time
285 | 285 | EFan1Prv | Hanson\CX2\RTU2S | rtu2s | 10.1.13.71/pe/rtu2s.xml | On |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool |  | Supply Air Temperature Setpoint | RTU2S was not created in SkySpark
286 | 286 | FreezeStat | Hanson\CX2\RTU2S | rtu2s | 10.1.13.71/pe/rtu2s.xml | Off |  | 1 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Bool |  | Today's Start Time
287 | 287 | PhaseProtection | Hanson\CX2\RTU2S | rtu2s | 10.1.13.71/pe/rtu2s.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool |  | Scheduled Start Time
288 | 288 | SFanPrv | Hanson\CX2\RTU2S | rtu2s | 10.1.13.71/pe/rtu2s.xml | On |  | 1 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Bool |  | Scheduled Stop Time
289 | 289 | SFanVFDTrouble | Hanson\CX2\RTU2S | rtu2s | 10.1.13.71/pe/rtu2s.xml | On |  | 1 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Bool
290 | 290 | AdjStPt | Hanson\CX2\VAV101 | vav101 | 10.1.13.71/pe/vav101.xml | -1.93 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav101.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
291 | 291 | DAT | Hanson\CX2\VAV101 | vav101 | 10.1.13.71/pe/vav101.xml | 58.6 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
292 | 292 | RMT | Hanson\CX2\VAV101 | vav101 | 10.1.13.71/pe/vav101.xml | 71.2 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
293 | 293 | VP | Hanson\CX2\VAV101 | vav101 | 10.1.13.71/pe/vav101.xml | 0.04 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
294 | 294 | AdjStPt | Hanson\CX2\VAV102 | vav102 | 10.1.13.71/pe/vav102.xml | -1.94 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav102.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
295 | 295 | DAT | Hanson\CX2\VAV102 | vav102 | 10.1.13.71/pe/vav102.xml | 62.7 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
296 | 296 | RMT_A | Hanson\CX2\VAV102 | vav102 | 10.1.13.71/pe/vav102.xml | 70.5 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
297 | 297 | RMT_B | Hanson\CX2\VAV102 | vav102 | 10.1.13.71/pe/vav102.xml | 70.7 | °F | 1000 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Number | fahrenheit
298 | 298 | VP | Hanson\CX2\VAV102 | vav102 | 10.1.13.71/pe/vav102.xml | 0.05 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
299 | 299 | AdjStPt | Hanson\CX2\VAV103 | vav103 | 10.1.13.71/pe/vav103.xml | 0.8 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav103.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
300 | 300 | DAT | Hanson\CX2\VAV103 | vav103 | 10.1.13.71/pe/vav103.xml | 65.1 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
301 | 301 | RMT | Hanson\CX2\VAV103 | vav103 | 10.1.13.71/pe/vav103.xml | 71.3 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
302 | 302 | VP | Hanson\CX2\VAV103 | vav103 | 10.1.13.71/pe/vav103.xml | 0.02 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
303 | 303 | AdjStPt | Hanson\CX2\VAV104 | vav104 | 10.1.13.71/pe/vav104.xml | 0.05 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav104.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
304 | 304 | DAT | Hanson\CX2\VAV104 | vav104 | 10.1.13.71/pe/vav104.xml | 69.2 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
305 | 305 | OvrA | Hanson\CX2\VAV104 | vav104 | 10.1.13.71/pe/vav104.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool
306 | 306 | OvrB | Hanson\CX2\VAV104 | vav104 | 10.1.13.71/pe/vav104.xml | Off |  | 1 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Bool
307 | 307 | RMT | Hanson\CX2\VAV104 | vav104 | 10.1.13.71/pe/vav104.xml | 71.2 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
308 | 308 | VP | Hanson\CX2\VAV104 | vav104 | 10.1.13.71/pe/vav104.xml | 0.1 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
309 | 309 | AdjStPt | Hanson\CX2\VAV105 | vav105 | 10.1.13.71/pe/vav105.xml | -1.69 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav105.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
310 | 310 | DAT | Hanson\CX2\VAV105 | vav105 | 10.1.13.71/pe/vav105.xml | 69.7 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
311 | 311 | RMT | Hanson\CX2\VAV105 | vav105 | 10.1.13.71/pe/vav105.xml | 70.8 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
312 | 312 | VP | Hanson\CX2\VAV105 | vav105 | 10.1.13.71/pe/vav105.xml | 0.08 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
313 | 313 | AdjStPt | Hanson\CX2\VAV106 | vav106 | 10.1.13.71/pe/vav106.xml | 1.32 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav106.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
314 | 314 | DAT | Hanson\CX2\VAV106 | vav106 | 10.1.13.71/pe/vav106.xml | 66.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
315 | 315 | RMT | Hanson\CX2\VAV106 | vav106 | 10.1.13.71/pe/vav106.xml | 72.4 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
316 | 316 | VP | Hanson\CX2\VAV106 | vav106 | 10.1.13.71/pe/vav106.xml | 0.09 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
317 | 317 | Ovr | Hanson\CX2\VAV106 | vav106 | 10.1.13.71/pe/vav106.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool
318 | 318 | AdjStPt | Hanson\CX2\VAV107 | vav107 | 10.1.13.71/pe/vav107.xml | 2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav107.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
319 | 319 | DAT | Hanson\CX2\VAV107 | vav107 | 10.1.13.71/pe/vav107.xml | 56.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
320 | 320 | Ovr | Hanson\CX2\VAV107 | vav107 | 10.1.13.71/pe/vav107.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool
321 | 321 | RMT | Hanson\CX2\VAV107 | vav107 | 10.1.13.71/pe/vav107.xml | 75.2 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
322 | 322 | VP | Hanson\CX2\VAV107 | vav107 | 10.1.13.71/pe/vav107.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
323 | 323 | AdjStPt | Hanson\CX2\VAV108 | vav108 | 10.1.13.71/pe/vav108.xml | 2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav108.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
324 | 324 | DAT | Hanson\CX2\VAV108 | vav108 | 10.1.13.71/pe/vav108.xml | 74.9 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
325 | 325 | RMT_A | Hanson\CX2\VAV108 | vav108 | 10.1.13.71/pe/vav108.xml | 71.5 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
326 | 326 | RMT_B | Hanson\CX2\VAV108 | vav108 | 10.1.13.71/pe/vav108.xml | 71.5 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
327 | 327 | VP | Hanson\CX2\VAV108 | vav108 | 10.1.13.71/pe/vav108.xml | 0.12 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
328 | 328 | AdjStPt | Hanson\CX2\VAV109 | vav109 | 10.1.13.71/pe/vav109.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav109.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
329 | 329 | DAT | Hanson\CX2\VAV109 | vav109 | 10.1.13.71/pe/vav109.xml | 57 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
330 | 330 | RMT | Hanson\CX2\VAV109 | vav109 | 10.1.13.71/pe/vav109.xml | 70.8 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
331 | 331 | VP | Hanson\CX2\VAV109 | vav109 | 10.1.13.71/pe/vav109.xml | 0.07 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
332 | 332 | AdjStPt | Hanson\CX2\VAV110 | vav110 | 10.1.13.71/pe/vav110.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav110.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
333 | 333 | DAT | Hanson\CX2\VAV110 | vav110 | 10.1.13.71/pe/vav110.xml | 56.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
334 | 334 | RMT | Hanson\CX2\VAV110 | vav110 | 10.1.13.71/pe/vav110.xml | 71.5 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
335 | 335 | VP | Hanson\CX2\VAV110 | vav110 | 10.1.13.71/pe/vav110.xml | 0.04 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
336 | 336 | AdjStPt | Hanson\CX2\VAV111 | vav111 | 10.1.13.71/pe/vav111.xml | -1.2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav111.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
337 | 337 | DAT | Hanson\CX2\VAV111 | vav111 | 10.1.13.71/pe/vav111.xml | 56.3 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
338 | 338 | RMT | Hanson\CX2\VAV111 | vav111 | 10.1.13.71/pe/vav111.xml | 71.5 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
339 | 339 | VP | Hanson\CX2\VAV111 | vav111 | 10.1.13.71/pe/vav111.xml | 0.14 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
340 | 340 | AdjStPt | Hanson\CX2\VAV112 | vav112 | 10.1.13.71/pe/vav112.xml | -0.04 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav112.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
341 | 341 | DAT | Hanson\CX2\VAV112 | vav112 | 10.1.13.71/pe/vav112.xml | 67.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
342 | 342 | RMT | Hanson\CX2\VAV112 | vav112 | 10.1.13.71/pe/vav112.xml | 72.4 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
343 | 343 | VP | Hanson\CX2\VAV112 | vav112 | 10.1.13.71/pe/vav112.xml | 0.11 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
344 | 344 | AdjStPt | Hanson\CX2\VAV113 | vav113 | 10.1.13.71/pe/vav113.xml | 2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav113.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
345 | 345 | DAT | Hanson\CX2\VAV113 | vav113 | 10.1.13.71/pe/vav113.xml | 74.9 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
346 | 346 | Ovr | Hanson\CX2\VAV113 | vav113 | 10.1.13.71/pe/vav113.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool
347 | 347 | RMT | Hanson\CX2\VAV113 | vav113 | 10.1.13.71/pe/vav113.xml | 74.1 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
348 | 348 | VP | Hanson\CX2\VAV113 | vav113 | 10.1.13.71/pe/vav113.xml | 0.13 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
349 | 349 | AdjStPt | Hanson\CX2\VAV114 | vav114 | 10.1.13.71/pe/vav114.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav114.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
350 | 350 | DAT | Hanson\CX2\VAV114 | vav114 | 10.1.13.71/pe/vav114.xml | 55.1 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
351 | 351 | RMT | Hanson\CX2\VAV114 | vav114 | 10.1.13.71/pe/vav114.xml | 74.1 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
352 | 352 | VP | Hanson\CX2\VAV114 | vav114 | 10.1.13.71/pe/vav114.xml | 0.01 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
353 | 353 | AdjStPt | Hanson\CX2\VAV201 | vav201 | 10.1.13.71/pe/vav201.xml | 1.97 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav201.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
354 | 354 | DAT | Hanson\CX2\VAV201 | vav201 | 10.1.13.71/pe/vav201.xml | 69.4 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
355 | 355 | RMT | Hanson\CX2\VAV201 | vav201 | 10.1.13.71/pe/vav201.xml | 72.4 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
356 | 356 | VP | Hanson\CX2\VAV201 | vav201 | 10.1.13.71/pe/vav201.xml | 0.01 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
357 | 357 | AdjStPt | Hanson\CX2\VAV202 | vav202 | 10.1.13.71/pe/vav202.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav202.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
358 | 358 | DAT | Hanson\CX2\VAV202 | vav202 | 10.1.13.71/pe/vav202.xml | 55.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
359 | 359 | RMT | Hanson\CX2\VAV202 | vav202 | 10.1.13.71/pe/vav202.xml | 71.9 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
360 | 360 | VP | Hanson\CX2\VAV202 | vav202 | 10.1.13.71/pe/vav202.xml | 0.06 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
361 | 361 | AdjStPt | Hanson\CX2\VAV203 | vav203 | 10.1.13.71/pe/vav203.xml | -0.94 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav203.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
362 | 362 | DAT | Hanson\CX2\VAV203 | vav203 | 10.1.13.71/pe/vav203.xml | 64.8 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
363 | 363 | RMT | Hanson\CX2\VAV203 | vav203 | 10.1.13.71/pe/vav203.xml | 71.5 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
364 | 364 | VP | Hanson\CX2\VAV203 | vav203 | 10.1.13.71/pe/vav203.xml | 0.02 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
365 | 365 | AdjStPt | Hanson\CX2\VAV204 | vav204 | 10.1.13.71/pe/vav204.xml | NotSet |  | 1 | Disabled | 0 | 2 | 10.1.13.71/pe/vav204.xml | airTerminalUnit, vav | his, point, writable, sensor | Str
366 | 366 | DAT | Hanson\CX2\VAV204 | vav204 | 10.1.13.71/pe/vav204.xml | 74.7 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
367 | 367 | RMT | Hanson\CX2\VAV204 | vav204 | 10.1.13.71/pe/vav204.xml | 72.2 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
368 | 368 | VP | Hanson\CX2\VAV204 | vav204 | 10.1.13.71/pe/vav204.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
369 | 369 | AdjStPt | Hanson\CX2\VAV205 | vav205 | 10.1.13.71/pe/vav205.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav205.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
370 | 370 | DAT | Hanson\CX2\VAV205 | vav205 | 10.1.13.71/pe/vav205.xml | 63.2 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
371 | 371 | RMT | Hanson\CX2\VAV205 | vav205 | 10.1.13.71/pe/vav205.xml | 70.7 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
372 | 372 | VP | Hanson\CX2\VAV205 | vav205 | 10.1.13.71/pe/vav205.xml | 0.02 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
373 | 373 | AdjStPt | Hanson\CX2\VAV206A | vav206a | 10.1.13.71/pe/vav206a.xml | -1.2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav206a.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
374 | 374 | DAT | Hanson\CX2\VAV206A | vav206a | 10.1.13.71/pe/vav206a.xml | 57.2 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
375 | 375 | RMT | Hanson\CX2\VAV206A | vav206a | 10.1.13.71/pe/vav206a.xml | 72.4 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
376 | 376 | VP | Hanson\CX2\VAV206A | vav206a | 10.1.13.71/pe/vav206a.xml | 0.04 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
377 | 377 | DAT | Hanson\CX2\VAV206B | vav206b | 10.1.13.71/pe/vav206b.xml | 61.7 | °F | 1000 | Enabled | 0 | 4 | 10.1.13.71/pe/vav206b.xml | airTerminalUnit, vav | his, point, writable, sensor | Number | fahrenheit
378 | 378 | Ovr | Hanson\CX2\VAV206B | vav206b | 10.1.13.71/pe/vav206b.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool
379 | 379 | VP | Hanson\CX2\VAV206B | vav206b | 10.1.13.71/pe/vav206b.xml | 0.05 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
380 | 380 | AdjStPt | Hanson\CX2\VAV207 | vav207 | 10.1.13.71/pe/vav207.xml | -1.91 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav207.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
381 | 381 | DAT | Hanson\CX2\VAV207 | vav207 | 10.1.13.71/pe/vav207.xml | 54.6 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
382 | 382 | RMT | Hanson\CX2\VAV207 | vav207 | 10.1.13.71/pe/vav207.xml | 70.7 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
383 | 383 | VP | Hanson\CX2\VAV207 | vav207 | 10.1.13.71/pe/vav207.xml | 0.31 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
384 | 384 | AdjStPt | Hanson\CX2\VAV208 | vav208 | 10.1.13.71/pe/vav208.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav208.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
385 | 385 | DAT | Hanson\CX2\VAV208 | vav208 | 10.1.13.71/pe/vav208.xml | 54.6 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
386 | 386 | Ovr | Hanson\CX2\VAV208 | vav208 | 10.1.13.71/pe/vav208.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool
387 | 387 | RMT | Hanson\CX2\VAV208 | vav208 | 10.1.13.71/pe/vav208.xml | 70.7 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
388 | 388 | VP | Hanson\CX2\VAV208 | vav208 | 10.1.13.71/pe/vav208.xml | 0.14 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
389 | 389 | AdjStPt | Hanson\CX2\VAV209 | vav209 | 10.1.13.71/pe/vav209.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav209.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
390 | 390 | DAT | Hanson\CX2\VAV209 | vav209 | 10.1.13.71/pe/vav209.xml | 60.3 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
391 | 391 | RMT | Hanson\CX2\VAV209 | vav209 | 10.1.13.71/pe/vav209.xml | 69.6 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
392 | 392 | VP | Hanson\CX2\VAV209 | vav209 | 10.1.13.71/pe/vav209.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
393 | 393 | AdjStPt | Hanson\CX2\VAV210 | vav210 | 10.1.13.71/pe/vav210.xml | 2 |  | 1000 | Enabled | 0 | 1 | 10.1.13.71/pe/vav210.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
394 | 394 | DAT | Hanson\CX2\VAV210 | vav210 | 10.1.13.71/pe/vav210.xml | 82.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
395 | 395 | RMT | Hanson\CX2\VAV210 | vav210 | 10.1.13.71/pe/vav210.xml | 73.1 | °F | 1000 | Enabled | 0 | 2 |  |  | his, point, writable, sensor | Number | fahrenheit
396 | 396 | VP | Hanson\CX2\VAV210 | vav210 | 10.1.13.71/pe/vav210.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
397 | 397 | Ovr | Hanson\CX2\VAV210 | vav210 | 10.1.13.71/pe/vav210.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool
398 | 398 | AdjStPt | Hanson\CX2\VAV211A | vav211a | 10.1.13.71/pe/vav211a.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav211a.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
399 | 399 | DAT | Hanson\CX2\VAV211A | vav211a | 10.1.13.71/pe/vav211a.xml | 56.9 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
400 | 400 | RMT | Hanson\CX2\VAV211A | vav211a | 10.1.13.71/pe/vav211a.xml | 73.2 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
401 | 401 | VP | Hanson\CX2\VAV211A | vav211a | 10.1.13.71/pe/vav211a.xml | 0.06 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
402 | 402 | AdjStPt | Hanson\CX2\VAV211B | vav211b | 10.1.13.71/pe/vav211b.xml | -1.97 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav211b.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
403 | 403 | DAT | Hanson\CX2\VAV211B | vav211b | 10.1.13.71/pe/vav211b.xml | 62.7 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
404 | 404 | RMT | Hanson\CX2\VAV211B | vav211b | 10.1.13.71/pe/vav211b.xml | 71.7 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
405 | 405 | VP | Hanson\CX2\VAV211B | vav211b | 10.1.13.71/pe/vav211b.xml | 0.03 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
406 | 406 | AdjStPt | Hanson\CX2\VAV212 | vav212 | 10.1.13.71/pe/vav212.xml | 1.22 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav212.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
407 | 407 | DAT | Hanson\CX2\VAV212 | vav212 | 10.1.13.71/pe/vav212.xml | 66.8 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
408 | 408 | Ovr | Hanson\CX2\VAV212 | vav212 | 10.1.13.71/pe/vav212.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool
409 | 409 | RMT | Hanson\CX2\VAV212 | vav212 | 10.1.13.71/pe/vav212.xml | 72.9 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
410 | 410 | VP | Hanson\CX2\VAV212 | vav212 | 10.1.13.71/pe/vav212.xml | 0.42 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
411 | 411 | AdjStPt | Hanson\CX2\VAV213 | vav213 | 10.1.13.71/pe/vav213.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav213.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
412 | 412 | DAT | Hanson\CX2\VAV213 | vav213 | 10.1.13.71/pe/vav213.xml | 69.4 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
413 | 413 | Ovr | Hanson\CX2\VAV213 | vav213 | 10.1.13.71/pe/vav213.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool
414 | 414 | RMT_A | Hanson\CX2\VAV213 | vav213 | 10.1.13.71/pe/vav213.xml | 70.8 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
415 | 415 | RMT_B | Hanson\CX2\VAV213 | vav213 | 10.1.13.71/pe/vav213.xml | 71.3 | °F | 1000 | Enabled | 0 | 5 |  |  | his, point, writable, sensor | Number | fahrenheit
416 | 416 | VP | Hanson\CX2\VAV213 | vav213 | 10.1.13.71/pe/vav213.xml | 0.32 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
417 | 417 | AdjStPt | Hanson\CX2\VAV214 | vav214 | 10.1.13.71/pe/vav214.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav214.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
418 | 418 | DAT | Hanson\CX2\VAV214 | vav214 | 10.1.13.71/pe/vav214.xml | 58.9 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
419 | 419 | RMT | Hanson\CX2\VAV214 | vav214 | 10.1.13.71/pe/vav214.xml | 74.5 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
420 | 420 | VP | Hanson\CX2\VAV214 | vav214 | 10.1.13.71/pe/vav214.xml | 0.22 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
421 | 421 | AdjStPt | Hanson\CX2\VAV215 | vav215 | 10.1.13.71/pe/vav215.xml | -0.95 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav215.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
422 | 422 | DAT | Hanson\CX2\VAV215 | vav215 | 10.1.13.71/pe/vav215.xml | 59.3 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
423 | 423 | RMT | Hanson\CX2\VAV215 | vav215 | 10.1.13.71/pe/vav215.xml | 69.8 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
424 | 424 | VP | Hanson\CX2\VAV215 | vav215 | 10.1.13.71/pe/vav215.xml | 0.1 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
425 | 425 | AdjStPt | Hanson\CX2\VAV216 | vav216 | 10.1.13.71/pe/vav216.xml | -1.84 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav216.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
426 | 426 | DAT | Hanson\CX2\VAV216 | vav216 | 10.1.13.71/pe/vav216.xml | 65.8 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
427 | 427 | RMT | Hanson\CX2\VAV216 | vav216 | 10.1.13.71/pe/vav216.xml | 71.7 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
428 | 428 | VP | Hanson\CX2\VAV216 | vav216 | 10.1.13.71/pe/vav216.xml | 0.33 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
429 | 429 | over | Hanson\CX2\VAV216 | vav216 | 10.1.13.71/pe/vav216.xml | Off |  | 1 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Bool
430 | 430 | AdjStPt | Hanson\CX2\VAV217 | vav217 | 10.1.13.71/pe/vav217.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav217.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
431 | 431 | DAT | Hanson\CX2\VAV217 | vav217 | 10.1.13.71/pe/vav217.xml | 59.5 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
432 | 432 | RMT | Hanson\CX2\VAV217 | vav217 | 10.1.13.71/pe/vav217.xml | 69.8 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
433 | 433 | VP | Hanson\CX2\VAV217 | vav217 | 10.1.13.71/pe/vav217.xml | 0.19 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number
434 | 434 | AdjStPt | Hanson\CX2\VAV218 | vav218 | 10.1.13.71/pe/vav218.xml | -2 |  | 1000 | Enabled | 0 | 2 | 10.1.13.71/pe/vav218.xml | airTerminalUnit, vav | his, point, writable, sensor | Number
435 | 435 | DAT | Hanson\CX2\VAV218 | vav218 | 10.1.13.71/pe/vav218.xml | 53.7 | °F | 1000 | Enabled | 0 | 4 |  |  | his, point, writable, sensor | Number | fahrenheit
436 | 436 | RMT_A | Hanson\CX2\VAV218 | vav218 | 10.1.13.71/pe/vav218.xml | 70 | °F | 1000 | Enabled | 0 | 1 |  |  | his, point, writable, sensor | Number | fahrenheit
437 | 437 | RMT_B | Hanson\CX2\VAV218 | vav218 | 10.1.13.71/pe/vav218.xml | 71.4 | °F | 1000 | Enabled | 0 | 3 |  |  | his, point, writable, sensor | Number | fahrenheit
438 | 438 | VP | Hanson\CX2\VAV218 | vav218 | 10.1.13.71/pe/vav218.xml | 0.29 |  | 1000 | Enabled | 0 | 7 |  |  | his, point, writable, sensor | Number

## Unit _Table
°F | fahrenheit | https://www.project-haystack.org/download/units.txt
ppm | parts_per_million
Rh | percent_relative_humidity